## Slide 1
Course on Bulking Sludge
Bulking Sludge:
Laboratory Investigations
Mark C.M. van Loosdrecht

## Slide 2
Bulking sludge causes
PROCESS CONTROL
KINETICS
SLUDGE BULKING
HYDRODYNAMICS
STORAGE
FOAMING OR
SCUMMING
FEEDING
PATTERN
MICROBIAL PHISIOLOGY
FISH, DGGE, PCR
MOLECULAR MICROBIOLOGY
PIN POINT FLOCS
BLANKET
RISISNG
OPERATIONAL PARAMETERS:
WASTEWATER
COMPOSITION
EPS
MODELING
CHAOTIC
BEHAVIOR OF AS
EM, CLSM, Flow Cit.
FILAMENTS a, b, c, …
WHO EATS WHAT?
TRANSPORT PROCESSES
SLUDGE
SETTLEABILTY
Martins, A. M., Pagilla, K., Heijnen, J. J., & van Loosdrecht, M. C. (2004). Filamentous bulking sludge—a critical review. Water research, 38(4), 793-817.

## Slide 3
?
Scale-down approach

## Slide 4
Scale-down approach
Make a system where bacteria experience the same as on large scale
Regime analysis
Time constants
Select substrate
SBR is ideal tool

## Slide 5
…
…
…
Influent
Effluent
Waste sludge
Return sludge
Cascade tanks - PFR
Influent
Effluent
Waste sludge
Return sludge
Settler/ Thickener
CSTR
[S]
Direction of flow
Continuous feed … long time
Feed phase
Direction of flow / Cycle time
[S]
Feed
Air, N2
Feed
Air, N2
SBR’s
Pulse feed … few minutes
Cycle time
[S]
Bulking sludge study

## Slide 6
Mixing
0
10
...
13
203
Fill (aerated)
React
201
Sludge wastage
233
Settle
240
Draw
Cycle time (min)
Cycles of 4 h
HRT = 8 h
SRT = 10 days (not always possible)
Csource: Acetic acid (150, 300 mg TOC/l influent)
Length of the feed phase: 3, 10, … 193 min
[O2]feast phase: 0.2, 0.7-1.1, >2.5 mg O2/l
Bulking sludge research
Martins, A. M., Heijnen, J. J., & van Loosdrecht, M. C. (2004). Bulking sludge in biological nutrient removal systems. Biotechnology and bioengineering, 86(2), 125-135.

## Slide 7
Increasing the length
of the feed phase
Low substrate concentration
in the reactor
Deterioration of
the sludge settleability
Low gradient of
Substrate over time
The results are reproducible
Size of aerobic selector
Feed time
Martins, A. M., Heijnen, J. J., & Van Loosdrecht, M. C. (2003). Effect of feeding pattern and storage on the sludge settleability under aerobic conditions. Water Research, 37(11), 2555-2570.

## Slide 8
  Finger type structures
Sphaerotilus natans
Too small selector
  Filaments abundant

## Slide 9
Low bulk liquid DO concentration in the feast phase
[O2] < 0.5 mg/l. cc
Deterioration of the sludge settleability
Abundance of filaments in the sludge / open floc structures
Effect of aeration
Martins, A. M. P., Heijnen, J. J., & Van Loosdrecht, M. C. M. (2003). Effect of dissolved oxygen concentration on sludge settleability. Applied microbiology and biotechnology, 62, 586-593.

## Slide 10
Reproducible results.
< [O2]feast phase has a strong negative impact on the sludge settleability.
Combined low DO and low substrate concentration: Less effect!
Shift in the dominant filament at different bulk liquid [O2]feast phase. Why?
Effect of aeration
< [O2]feast phase
Pulse feeding
< [O2]feast phase
>2.5
Prolonged feeding
< [O2]feast phase

## Slide 11
  -qsmax bulking sludge  -qsmax well settling sludge
Not in accordance with the kinetic selection theory
qpmax bulking sludge  qpmax well settling sludge
Specific substrate uptake rate:
Specific PHB production rate:
Ks, fil < Ks, floc
Low [S]: -qs, fil > -qs, floc
High [S]: -qs, fil < -qs, floc
Bulking sludge theory
  Kinetic selection theory

## Slide 12
Decreasing substrate concentration during substrate uptake
flocs > 500 mm after 1 month
Formation of granules
Few filaments
qs > 0.8·qsmax
Porous flocs
Finger type structures
Few filaments
qs= 0.6 to 0.8·qsmax
Finger type structures
Filaments are very common / abundant
qs < 0.6·qsmax
General observations
Martins, A. M., Pagilla, K., Heijnen, J. J., & van Loosdrecht, M. C. (2004). Filamentous bulking sludge—a critical review. Water research, 38(4), 793-817.

## Slide 13
Acetate as carbon source;
Aerobic conditions;
No nitrification/denitrification.
Occurrence
Martins, A. M., Pagilla, K., Heijnen, J. J., & van Loosdrecht, M. C. (2004). Filamentous bulking sludge—a critical review. Water research, 38(4), 793-817.

## Slide 14
Cycles of 6 h; HRT = 12 h; SRT = 10 days
Experiences to simulate:
Anoxic selector too big: low [SC].
Low [NO3-] in the anoxic tank.
0
Fill (anoxic)
135
300
Aerobic
298
Sludge wastage
350
Settle
360
Draw
Cycle time (min)
Denitrification

## Slide 15
Denitrification
No bulking in pure denitrifying conditions
Not at low nitrate and not at low substrate concentrations
- Also in literature no denitrifying filamentous bacterium described
- In laboratory and pilot systems: often not pure denitrifying conditions
Tampus, M. V., Martins, A. M. P., & Van Loosdrecht, M. C. M. (2004). The effect of anoxic selectors on sludge bulking. Water Science and Technology, 50(6), 261-268.

## Slide 16
0
Fill anaerobic
90
135
270
(Fill) Aerobic
268
Sludge wastage
350
Settle
360
Draw
Cycle time (min)
Cycles of 6 h; HRT = 12 h; SRT = 10 days
Experiments to simulate:
Anaerobic selector too big: low [SC].
Anaerobic selector too small: low [SC] in the aerobic stage.
...
195
Aerobic
Anaerobic selector

## Slide 17
Well settling sludge: SVI < 40 ml/g
No influence of substrate concentration
P-removing bacteria
Less sensitive to substrate leaks into aerobic phase
Anaerobic selectors

## Slide 18
What is the effect of particulate substrate on the sludge settleability?
Where does hydrolysis take place?
Process kinetics and role of storage?
Mixing
0
10
13
143
Fill (aerated)
React
141
Sludge wastage
233
Settle
240
Draw
Cycle time (min)
Polymer substrate
HRT = 8 h; SRT=10 days
Length of the feed phase: 3 min
Csource: soluble starch; native potato starch (150 mg/l TOC)
Pulse feed of soluble starch; native potato starch (sterilized and non-sterilized); glucose; maltose.
Martins, A. M., Karahan, Ö., & van Loosdrecht, M. C. (2011). Effect of polymeric substrate on sludge settleability.
Water Research, 45(1), 263-273..

## Slide 19
Polymer substrate
Starch is adsorbed on the biomass. Starch hydrolysis takes place mostly inside the floc/cell surface.
Filaments (Nostocoida limicola ) are excessive, and they grow as:
Native potato starch: SVI<100 ml/g
Soluble starch: SVI>150 ml/g
Martins, A. M., Karahan, Ö., & van Loosdrecht, M. C. (2011). Effect of polymeric substrate on sludge settleability.
Water Research, 45(1), 263-273..

## Slide 20
HRT = 24 h; SRT=20 days
Csource: tween 80
N-source: (NH4)2SO4
S-source: L-methionine
Length of the feed phase: 60 min
DO control (30% mass aerobic fraction):
Aerobic (DO<1.5 mg O2/l)
0
1
10
230
350
360
Cycle time (min)
…
Not aerated
Microthrix parvicella

## Slide 21
General reason for bulking is the combination of bacterial morphology and gradients of substrate concentration in sludge flocs (micro-gradients) due to diffusion-reaction-growth processes.
General theory

## Slide 22
3. Mass balance of substrate (diffusion + reaction):
RBL
W2
W1
Computational domain
Biomass particles
Grid elements
Bacterial cells are treated as single units
2. It can consider different spreading mechanisms
Modelling

## Slide 23
Modelling
Martins, A. M., Picioreanu, C., Heijnen, J. J., & Van Loosdrecht, M. C. (2004). Three-dimensional dual-morphotype species modeling of activated sludge flocs. Environmental science & technology, 38(21), 5632-5641.

## Slide 24
Low [O2]: 0.2 mgO2/l
Strong
micro-gradients
of substrate concentration
Floc-formers and filaments
Modelling
Martins, A. M., Picioreanu, C., Heijnen, J. J., & Van Loosdrecht, M. C. (2004). Three-dimensional dual-morphotype species modeling of activated sludge flocs. Environmental science & technology, 38(21), 5632-5641.

## Slide 25
General reason for sludge bulking is the combination of bacterial morphology and gradients of substrate concentration in sludge flocs (micro-gradients) due to diffusion-reaction-growth processes.
General solution is application of plug-flow (selector) systems properly designed, controlled, and operated.
Conclusion

## Slide 26
Course on Bulking Sludge
Acknowledgments
Cristian Picioreanu
Antonio Martins