## Slide 1
Course on Bulking Sludge
Bulking Sludge:
Practical Implications
Mark C.M. van Loosdrecht

## Slide 2
General reason for sludge bulking is the combination of bacterial morphology and gradients of substrate concentration in sludge flocs (micro-gradients) due to diffusion-reaction-growth processes.
General solution is application of plug-flow (selector) systems properly designed, controlled, and operated.
Intermediate Conclusion

## Slide 3
Ks, fil < Ks, floc
Low [S]: -qs, fil > -qs, floc
High [S]: -qs, fil < -qs, floc
Kinetic selection theory
(Chudoba et al., 1973)
Chudoba, J., Čech, J. S., Farkač, J., & Grau, P. (1985). Control of activated sludge filamentous bulking: experimental verification of a kinetic selection theory. Water Research, 19(2), 191-196.

## Slide 4
Selector
150 ml/g
Rensink, J. H. (1974). New approach to preventing bulking sludge. Journal (Water Pollution Control Federation), 1888-1894.

## Slide 5
Good solution ….. provided oxygen level can be maintained and plug flow conditions are ensured….
Summer/winter conditions
Industrial systems: very high oxygen demand
Aerobic selectors

## Slide 6
Good solution ….. provided nitrate is sufficient present….
Day-night regime
Low nitrate effluent
No oxygen intrusion
No problem with mixing
Anoxic selectors

## Slide 7
Good solution ….. provided oxygen intrusion is prevented….
No problem with respect to mixing
Seemingly very stable
P-removing bacteria not essential in this case
Anaerobic selectors

## Slide 8
Particulate/polymeric COD: situation still vague
Rapid change between aerated/non aerated conditions can lead to Microthrix problems
Uncertainties

## Slide 9
Dominant filament in extended aeration systems for nutrient removal
1 % of population gives already significant increased SVI
Hydrophobic, can lead to foaming
Growth on long chain fatty acids
Control
  Clear redox zones
  Low ammonium effluent
Microthrix parvicella
Nielsen, P. H., Roslev, P., Dueholm, T. E., & Nielsen, J. L. (2002). Microthrix parvicella, a specialized lipid consumer in anaerobic–aerobic activated sludge plants. Water Science and Technology, 46(1-2), 73-80.

## Slide 10: Dutch Design rules for advanced BNR and controll of SVI
Design temperature = 9-10°C
Contact time anaerobic reactor = 1 h, 4 compartments
Contact time anoxic selector = 0,3 h, 2-3 compartments
Seperate anoxic reactor
Recirculation flow rate total = 5-6 times QDWF
Control internal recirculation by redox, NO3 or NH4
Sludge age = 20 d, sludge loading = 0,010 kgN/kgDS.d
Always [O2] aerobic reactor = >1,5 mg/l; [NH4-N] < 1 mg/l
Division N-reactors based on Dutch/South Africa practice
Leusden, M. V., & Kruit, J. Inventarisatie richtlijnen en ervaringen voorkomen van slibuitspoeling op RWZI's.

## Slide 11
“In spite of all we learn and understand, some sludges will still bulk.”
(Albertson, 1991)
By unraveling the microbial physiology, improving the process design and the control of the sewage treatment plants we should be able to minimize this problem …or even create granular sludge.
Final remarks

## Slide 12
Course on Bulking Sludge
Acknowledgments
Jans Kruit
Antonio Martins