## Slide 1
Course on Aerobic Granular Sludge
Aerobic Granular Sludge
Introduction
Mark C.M. van Loosdrecht

## Slide 2
Contents
Developments of the technology
Principles of granular sludge formation
Utrecht Nereda WWTP
(credit: RoyalHaskoningDHV)

## Slide 3
Wastewater treatment plants
Large area usage
Complexity of settling
Replace clarifiers
No membranes

## Slide 4
Wastewater treatment - a history of biofilms vs flocs
1880: Introduction of biofilm processes
1914: Introduction of flocculent activated sludge

## Slide 5
Flocculent sludge systems dominant
Continuous development of biofilm processes
Wastewater treatment - a history of biofilms vs flocs

## Slide 6
Granular sludge process
- UASB
Upflow regime
Spontaneous granular sludge
Up to 40 kgCOD/m3.d
Granule offers ecological niche
Gatze Lettinga
G. Lettinga, A.G.N. Jansen, P. Terpstra (1975)
Anaerobe behandeling van suikerfabriek afvalwater, H2O, 8, p. 530

## Slide 7
Best of both worlds
Optimal biofilm/flocs combination
Easy, gravity driven, separation
High biomass concentration possible
High mass transfer area
Mixed reactors and no clogging
Structuring allows efficient microbial community design
Is granular sludge specific for
methanogenic systems,
or can all bacteria grow in granules?
Nicolella, C., van Loosdrecht, M. C., & Heijnen, S. J. (2000).
Particle-based biofilm reactor technology. Trends in Biotechnology, 18(7), 312-320.
Anaerobic IC reactor
Granular sludge process

## Slide 8
Microbiological explanation:
synthrophy, cell-cell communication, spaghetti-theory, etc.
Indeed, granules give nice ecological niche for anaerobic ecosystem, but granule formation is not based on microbial interactions.
Anaerobic granular sludge

## Slide 9
Modelling biofilm morphology from first principles
Picioreanu, C., Van Loosdrecht, M. C., & Heijnen, J. J. (2000) Effect of diffusive and convective substrate transport on biofilm structure formation: A two‐dimensional modeling study. Biotechnology and bioengineering, 69(5), 504-515.

## Slide 10: Reaction - diffusion - growth process
Substrate limitation
Vector field of substrate diffusion flux
Biofilm
Liquid
Biofilm
Liquid
Van Loosdrecht, M. C. M., Heijnen, J. J., Eberl, H., Kreft, J., & Picioreanu, C. (2002). Mathematical modelling of biofilm structures. Antonie van Leeuwenhoek, 81(1-4), 245-256.

## Slide 11: Morphogenesis of granules/biofilms
Biology is not needed to understand granular sludge formation
Biology is needed to understand the conversion processes in the reactors
High similarity in morphogenesis of crystals and biofilms/granules
Compact morphology
→ Slow rates (methanogens, Anammox)
→ No diffusion limited substrate uptake
→ Shear can counteract

## Slide 12: Basic aspects of Aerobic Granular Sludge Process
Need to select for slow growing bacteria
Based on phosphate accumulating bacteria
Sequencing batch operation
Anaerobic feeding – aerobic/anoxic phase
De Kreuk M.V. and Van Loosdrecht M.C.M. (2004). Selection of slow growing organisms as a means for improving aerobic granular sludge stability. Water Science and Technology, 49(11-12), 9-17.

## Slide 13
Pronk, M., Abbas, B., Al-Zuhairy, S.H.K., Kraan, R., Kleerebezem, R., & Van Loosdrecht, M.C.M. (2015). Effect and behaviour of different substrates in relation to the formation of aerobic granular sludge. Applied microbiology and biotechnology, 99(12), 5257-5268.

## Slide 14: Wastewater and granules
Soluble BOD: almost fully available for granular growth
Colloidal BOD: partly available for granular growth
Particular BOD: minimal available for granular growth
Soluble starch
Particulate starch
De Kreuk, M. K., Kishida, N., Tsuneda, S., & Van Loosdrecht, M. C. M. (2010). Behavior of polymeric substrates in an aerobic granular sludge system. Water research, 44(20), 5929-5938.

## Slide 15: Wastewater and granules
Soluble BOD not taken up anaerobically: filamentous bacteria/zoogloea
Colloidal and particular COD not used anaerobically ends up in floc fraction
→ denitrification and protozoa
De Kreuk, M. K., Kishida, N., Tsuneda, S., & Van Loosdrecht, M. C. M. (2010).
Behavior of polymeric substrates in an aerobic granular sludge system. Water research, 44(20), 5929-5938.

## Slide 16: Wastewater and granules
Full-scale aerobic granular sludge:
always a combination of flocs and granules
i.e. a hybrid process
Flocs: 2-5 days SRT
Granules: 30-50 days SRT
Flocs: influent bacteria and suspended solids
Bacteria growing on substrates not anaerobic converted
Granules: bacteria that grow in the reactor
Ali, M., Wang, Z., Salam, K.W., Hari, A.R., Pronk, M., Van Loosdrecht, M.C.M., & Saikaly, P.E. (2019). Importance of species sorting and immigration on the bacterial assembly of different-sized aggregates in a full-scale aerobic granular sludge plant. Environmental science & technology, 53(14), 8291-8301.

## Slide 17: Granulation
Van Dijk, E.J., Haaksman, V.A., van Loosdrecht, M.C.M., & Pronk, M. (2022). On the mechanisms for aerobic granulation-model based evaluation. Water Research, 216, 118365.
Competition with flocs
Selecting for bacteria with low maximal growth rate
→ storage specialist

## Slide 18
Van Dijk, E.J., Haaksman, V.A., van Loosdrecht, M.C.M., & Pronk, M. (2022).
On the mechanisms for aerobic granulation-model based evaluation. Water Research, 216, 118365.
Sludge population model:
individual based approach
Tracking lifecycle of particles
Different exposure to substrate between cycles.
For sufficient resolution of stochastic behavior: 10K-100K granule clusters,
Settling of clusters according to model of Van Dijk et al. (2020).

## Slide 19
Model of AGS start-up
Utrecht
Epe
Van Dijk, E.J., Haaksman, V.A., van Loosdrecht, M.C.M., & Pronk, M. (2022).
On the mechanisms for aerobic granulation-model based evaluation.
Water Research, 216, 118365.

## Slide 20: Sulphide -Thiotrix caldifontis
5% S-COD/l influent
33% S-COD/l Influent
0% mgS-COD/l influent
15% mgS-COD/l influent
25% mgS-COD/l influent
Selection of filamentous bacteria
- but still good granulation
De Graaff, D.R., van Loosdrecht, M.C.M., & Pronk, M. (2020). Stable granulation of seawater-adapted aerobic granular sludge with filamentous Thiothrix bacteria. Water Research, 175, 115683.

## Slide 21: Granular stability
Beun, J.J., Hendriks, A., Van Loosdrecht, M.C.M., Morgenroth, E., Wilderer, P.A., & Heijnen, J.J. (1999).
Aerobic granulation in a sequencing batch reactor. Water research, 33(10), 2283-2290.
Granular matrix is more stable than bacteria
Toxic shocks
Solubilisation 80°C and pH 9.5
Aerobically fed granules are instable!

## Slide 22: Endogenous process: no preferential turnover of EPS over biomass
Tomás-Martínez, S., Zwolsman, E.J., Merlier, F., Pabst, M., Lin, Y., Van Loosdrecht, M.C.M., & Weissbrodt, D.G. (2023). Turnover of the extracellular polymeric matrix of granules performing biological phosphate removal. Applied Microbiology and Biotechnology, 107(5), 1997-2009.
Sugars
Proteins

## Slide 23: Conclusion on AGS formation
AGS provides efficient wastewater treatment option.
Granulation is mainly based on reaction-diffusion principles:
Fast conversion gives flocs
Slow conversion gives granules
Main selection criteria:
Selective anaerobic feeding to granular sludge
Selective wasting of flocculent sludge
Full scale systems will always have a floc and granule fraction.

## Slide 24
Course on Aerobic Granular Sludge
Acknowledgments
Cristian Picioreanu
Merle de Kreuk
Mario Pronk
Helle van der Roest
And many PhD students
And RHDHV employees.