## Slide 1
Course on Aerobic Granular Sludge
Aerobic Granular Sludge
From Laboratory to Full-scale
Mark C.M. van Loosdrecht

## Slide 2
Contents
Scaling up of the technology
Implementation
Resource recovery

## Slide 3: Granular sludge
Every microorganism can grow in granular form
Slow growing type of microbes: easily to make granules (methanogens, nitrifiers, Anammox, PAO’s)
Fast growing microbes: difficult - need for shear etc.
(fermentative bacteria, aerobic heterotrophs)

## Slide 4: Granular sludge
Already widely applied in industry:
UASB, IC, EGSB and Circox technology
For municipal wastewater largest problem: hydraulic variation

## Slide 5: Selecting for well-settling sludge
Selector provides for well settling sludge:
SVI for conventional AS of 100-120 is very well possible
For EBPR around 80 could be feasible → preferred for granulation
For good granulation: selective feeding and selective sludge wasting
Martins, A.M., Pagilla, K., Heijnen, J.J., & van Loosdrecht, M.C.M. (2004).
Filamentous bulking sludge—a critical review. Water research, 38(4), 793-817.

## Slide 6
Cristian Picioreanu
Biofilm morphology
1996-1999
Antonio Martins
Activated sludge
morphology
1999-2003
Janneke Buen
Principle Granulation
1996-2000
Mario Pronk
Process eng. AGS
2002- (2010-2016)- ……
Mari Winkler
Microbiology AGS
2008-2012
Merle de Kreuk
Scale-up AGS
2000-(2005)-2009
Development of Nereda® technology - Academic

## Slide 7
Development of Nereda® technology – National Nereda® Research Program 2002

## Slide 8
Scale-down
Optimisation
Process
configuration
Simulation
Kinetics;
Process Insight
Laboratorium
Application
Scale-up
Design
Costs & Process
Production
Scale-up
Pilot
Testing,
Optimisation
Scale-up
Scale-up/scale-down approach

## Slide 9: Important design aspects for AGS selection
All readily biodegradable COD removed anaerobically.
Separation flocs and granules with short SRT for flocs.
Selective flocculent sludge withdrawal.
Not:
Shear
DO in aeration phase
Specific biological arguments (EPS/QS etc.)
Granule instability
→ Bottom feed: self-stabilizing principle

## Slide 10
Pronk, M., De Kreuk, M.K., De Bruin, B., Kamminga, P., Kleerebezem, R.V., & Van Loosdrecht, M.C.M. (2015).
Full scale performance of the aerobic granular sludge process for sewage treatment. Water Research, 84, 207-217.
Nereda®
Aerobic granular sludge (SBR) technology

## Slide 11
+ Constant influent and effluent to plant
+ Constant volume – no decanters, pump efficiency
+ No idle time or settling time
+ More even oxygen demand during aeration period
Nereda® vs SBR

## Slide 12
Nereda® configurations
Notes: Biopolymer  and you see that that granule also contain a biopolymer…is produced by the bacteria and actually an important reason why granules are obtained. The biopolymer is EPS especially produced by bacteria that able to store carbon under feast conditions, like the PAO’s and GAO’s that are present in normal activated sludge as well.

## Slide 13
Influent
and
Effluent
Nereda® cycle operation

## Slide 14
Baffle
Low N2
Increasing water depth
Low COD
Effluent gutter
High COD
Low N2
Decreasing water depth
Van Dijk, E.J., Pronk, M., & van Loosdrecht, M.C.M. (2020). A settling model for full-scale aerobic granular sludge. Water Research, 186, 116135.
Important differences
Density driven flow
Degassing
Nereda, Rushville Indiana
Settling – clarifier vs Nereda®

## Slide 15: Effect of N2 stripping
Van Dijk, E.J., Pronk, M., & van Loosdrecht, M.C.M. (2020). A settling model for full-scale aerobic granular sludge. Water Research, 186, 116135.

## Slide 16: Sludge consists of granules and flocs
Similarity with influent: flocs > small granules > large granules
The microbial communities in flocs were more dynamic than in granules as can be seen by their wider distribution.
Ali, M., Wang, Z., Salam, K.W., Hari, A.R., Pronk, M., Van Loosdrecht, M.C.M., & Saikaly, P.E. (2019).
Importance of species sorting and immigration on the bacterial assembly of different-sized aggregates in a full-scale aerobic granular sludge plant.
Environmental science & technology, 53(14), 8291-8301.

## Slide 17
https://nereda.royalhaskoningdhv.com/en/projects
Nereda® installations

## Slide 18: Garmerwolde WWTP
Nereda capacity: 140,000 p.e., 20 - 100 MLD (average 30)
Nereda reactors: 2 x 9,500 m3
Ntotal = 7 mg/l; Ptotal = 1 mg/l
Pronk, M., De Kreuk, M.K., De Bruin, B., Kamminga, P., Kleerebezem, R.V., & Van Loosdrecht, M.C.M. (2015).
Full scale performance of the aerobic granular sludge process for sewage treatment. Water Research, 84, 207-217.

## Slide 19
Utrecht WWTP
Originally constructed in 1976
Upgrade of existing CAS plant required (14 sedimentation tanks)
Capacity: 430,000 P.E.
6 Nereda reactors
  No separate anoxic, aerobic, and sedimentation stages
  No return sludge system
  Enhanced effluent quality
  Decommissioned area reclaimed by community for educational nature center
Existing aeration and sedimentation tanks demolished
Area repurposed as upgraded influent and solids handling facilities
Treats same capacity in < 40% footprint
Nereda® Utrecht replacement

## Slide 20
Test cell
94,000 P.E.
21,700 m3/day
Full plant upgrade
2,400,000 P.E.
159 MGD
Further examples: https://nereda.royalhaskoningdhv.com/en/applications/municipal-wastewater-treatment
Pronk, M., Giesen, A., Thompson, A., Robertson, S., & Van Loosdrecht, M.C.M. (2017).Aerobic granular biomass technology: advancements in design, applications and developments. Water Practice & Technology, 12(4), 987-996.
Nereda® Ringsend WWTP

## Slide 21
Seawater-adapted granules
8.00 mgP/gVSS.h for fresh water/seawater
2.90 mgP/gVSS.h for saline sater (NaCl)
Same PAO bacteria in
fresh water
saline water
seawater

## Slide 22: Extracellular polymeric substances (EPS)
Granules are bacteria embedded in EPS
Macropore
Accesible for all molecules
Semi-solid gel
Inaccesible for 10 kDa molecule?
Van den Berg, L., Ortega, S.T., van Loosdrecht, M.C.M., & de Kreuk, M.K. (2022). Diffusion of soluble organic substrates in aerobic granular sludge: Effect of molecular weight. Water Research X, 16, 100148.
Relevant for understanding
Not important for process
Option for resource recovery

## Slide 23: Present - EPS
Structural vs. non-structural polymers

## Slide 24: EPS consists of as yet not recognised polymers

## Slide 25: EPS as a resource
Large fraction of ‘waste sludge’
Limited oil-based competition
Biopolymer market supply limited
Potential market volume is larger
Many novel materials possible
Gel forming EPS from AGS: Kaumera®

## Slide 26: Aerobic Granular Sludge - Nereda® - Kaumera®
Roughly 120 Nereda® WWTP’s
More then double market volume of alginates

## Slide 27: New materials based on Kaumera®
Kim, N.K., Mao, N., Lin, R., Bhattacharyya, D., van Loosdrecht, M.C.M., & Lin, Y. (2020). Flame retardant property of flax fabrics coated by extracellular polymeric substances recovered from activated sludge and aerobic granular sludge. Water Research, 170, 115344.

## Slide 28: New materials based on Kaumera®
Stiffness comparable to fibre-reinforced polyesters
Yuemei Lin
https://www.youtube.com/watch?v=cC0-LYWHoXg

## Slide 29: Conclusions
Recognizing basic principles help to develop new technology
A strong collaboration ensured a smooth commercialization
Clear market advantages stimulate the introduction of novel technology
Potential for new forms of resource recovery

## Slide 30
Course on Aerobic Granular Sludge
Acknowledgments
Merle de Kreuk
Mario Pronk
Yuemei Lin
Helle van der Roest
And many PhD students
And RHDHV employees.