## Slide 1
Course on Aerobic Granular Sludge
AGS Plant Configuration and Design
Laurence Strubbe

## Slide 2
Worldwide implementation
Royal HaskoningDHV, 2023

## Slide 3
Plant design is case specific
Total plant volume is dependent on:
local influent flow rate and its variation
total COD and nitrogen load
water temperature
effluent requirements

## Slide 4
Plant design is case specific
Total plant volume is dependent on:
local influent flow rate and its variation
total COD and nitrogen load
water temperature
effluent requirements

## Slide 5
Plant design is case specific
Total plant volume is dependent on:
local influent flow rate and its variation
total COD and nitrogen load
water temperature
effluent requirements
wastewater characteristics

## Slide 6
General Plant design
Pre-treatment
Biological treatment
Post-treatment

## Slide 7
General Plant design
Pre-treatment
Biological treatment
Post-treatment

## Slide 8
General Plant design
Biological treatment
Post-treatment
Pre-treatment

## Slide 9
General Plant design
Post-treatment
Pre-treatment
Biological treatment

## Slide 10
General Plant design
Pre-treatment
Biological treatment
Post-treatment

## Slide 11
General Plant design
Pre-treatment
Biological treatment
Post-treatment
Similar to
activated sludge
Similar to
activated sludge

## Slide 12
General Plant design
Pre-treatment
Biological treatment
Post-treatment
Similar to
activated sludge
Differs from
activated sludge
Similar to
activated sludge

## Slide 13
General Plant design
Pre-treatment
Biological treatment
Post-treatment
Similar to
activated sludge
Differs from
activated sludge
Similar to
activated sludge
Topic of this course

## Slide 14
Plant configuration
Treatment of a continuous influent flow:

## Slide 15
Plant configuration
Treatment of a continuous influent flow:
Always one reactor in feeding mode
nreactor=

## Slide 16
Plant configuration
Treatment of a continuous influent flow:
Buffer tank
compensates for discontinuous feeding

## Slide 17
Plant configuration
Treatment of a continuous influent flow:
Hybrid:
activated sludge and aerobic granular sludge

## Slide 18
Overall design principle
Choose plant configuration
Calculate volume per reactor based on hydraulic and biological constraints
Choose limiting volume
Calculate reactor dimensions
Calculate buffer volume (if needed)
Calculate total plant volume

## Slide 19
Overall design principle
Choose plant configuration
Calculate volume per reactor based on hydraulic and biological constraints
Choose limiting volume
Calculate reactor dimensions
Calculate buffer volume (if needed)
Calculate total plant volume

## Slide 20
Plant configuration
Treatment of a continuous influent flow:

## Slide 21
Plant configuration
Treatment of a continuous influent flow:

## Slide 22
Plant configuration
Treatment of a continuous influent flow:

## Slide 23
Plant configuration
Treatment of a continuous influent flow:

## Slide 24
Overall design principle
Choose plant configuration
Calculate volume per reactor based on hydraulic and biological constraints
Choose limiting volume
Calculate reactor dimensions
Calculate buffer volume (if needed)
Calculate total plant volume

## Slide 25
Overall design principle
Choose plant configuration
Calculate volume per reactor based on hydraulic and biological constraints
Choose limiting volume
Calculate reactor dimensions
Calculate buffer volume (if needed)
Calculate total plant volume

## Slide 26
Overall design principle
Choose plant configuration
Calculate volume per reactor based on hydraulic and biological constraints
Choose limiting volume
Calculate reactor dimensions
Calculate buffer volume (if needed)
Calculate total plant volume

## Slide 27
Design volume
based on hydraulic constraints
Fill & draw phase

## Slide 28
Design volume
based on hydraulic constraints
= 1 h during DWF
Fill & draw phase

## Slide 29
Design volume
based on hydraulic constraints
65%
= 1 h during DWF
Fill & draw phase

## Slide 30
Design volume
based on hydraulic constraints
Vreactor,hyd =
Vreactor,hyd Reactor volume (m3)
65%
= 1 h during DWF
Fill & draw phase

## Slide 31
Design volume
based on hydraulic constraints
Vreactor,hyd =
Vreactor,hyd Reactor volume (m3)
Flow rate (m3.h-1)
65%
= 1 h during DWF
Fill & draw phase

## Slide 32
Design volume
based on hydraulic constraints
Vreactor,hyd =
Vreactor,hyd Reactor volume (m3)
Flow rate (m3.h-1)
Feeding time (1 h during DWF)
65%
= 1 h during DWF
Fill & draw phase

## Slide 33
Design volume
based on hydraulic constraints
Vreactor,hyd = =
Vreactor,hyd Reactor volume (m3)
Flow rate (m3.h-1)
Feeding time (1 h during DWF)
Batch volume (m3)
65%
= 1 h during DWF
Fill & draw phase

## Slide 34
Design volume
based on hydraulic constraints
Vreactor,hyd = =
Vreactor,hyd Reactor volume (m3)
Flow rate (m3.h-1)
Feeding time (1 h during DWF)
Batch volume (m3)
Maximal volume exchange ratio (= 65%)
to prevent high effluent concentrations
65%
= 1 h during DWF
Fill & draw phase

## Slide 35
Design volume
based on biological constraints
65%
Reaction phase

## Slide 36
Design volume
based on biological constraints
65%
Reaction phase
(h)

## Slide 37
Design volume
based on biological constraints
65%
Reaction phase
SLR (kg COD.kg-1 TSS.d-1)

## Slide 38
Design volume
based on biological constraints
65%
Reaction phase
SLR (kg COD.kg-1 TSS.d-1)
MLSS (8 kg.m-3)

## Slide 39
Design volume
based on biological constraints
MAX. SLR (kg COD.kg-1 TSS.d-1)
65%
Reaction phase
SLR (kg COD.kg-1 TSS.d-1)
MLSS (8 kg.m-3)

## Slide 40
Design volume
based on biological constraints
MAX. SLR (kg COD.kg-1 TSS.d-1)
is dependent on - wastewater temperature
- effluent requirements
65%
Reaction phase
SLR (kg COD.kg-1 TSS.d-1)
MLSS (8 kg.m-3)

## Slide 41
Design volume
based on biological constraints
MAX. SLR (kg COD.kg-1 TSS.d-1)
is dependent on - wastewater temperature
- effluent requirements
65%
Reaction phase
SLR (kg COD.kg-1 TSS.d-1)
MLSS (8 kg.m-3)
Nitrification occurs until 0.4 kg COD.kg-1 TSS.d-1 at moderate temperatures. Higher temperatures could allow nitrification even with higher loading rates.

## Slide 42
Design volume
based on biological constraints
MAX. SLR (kg COD.kg-1 TSS.d-1)
is dependent on - wastewater temperature
- effluent requirements
65%
Reaction phase
SLR (kg COD.kg-1 TSS.d-1)
MLSS (8 kg.m-3)
Nitrification occurs until 0.4 kg COD.kg-1 TSS.d-1 at moderate temperatures. Higher temperatures could allow nitrification even with higher loading rates.
=

## Slide 43
Design volume
based on biological constraints
MAX. SLR (kg COD.kg-1 TSS.d-1)
is dependent on - wastewater temperature
- effluent requirements
65%
Reaction phase
SLR (kg COD.kg-1 TSS.d-1)
MLSS (8 kg.m-3)
Nitrification occurs until 0.4 kg COD.kg-1 TSS.d-1 at moderate temperatures. Higher temperatures could allow nitrification even with higher loading rates.
=
Q Flow rate (m3.d-1)

## Slide 44
Design volume
based on biological constraints
MAX. SLR (kg COD.kg-1 TSS.d-1)
is dependent on - wastewater temperature
- effluent requirements
65%
Reaction phase
SLR (kg COD.kg-1 TSS.d-1)
MLSS (8 kg.m-3)
Nitrification occurs until 0.4 kg COD.kg-1 TSS.d-1 at moderate temperatures. Higher temperatures could allow nitrification even with higher loading rates.
=
Q Flow rate (m3.d-1)
COD COD concentration (kg.m-3)

## Slide 45
Design volume
based on biological constraints
MAX. SLR (kg COD.kg-1 TSS.d-1)
is dependent on - wastewater temperature
- effluent requirements
65%
Reaction phase
SLR (kg COD.kg-1 TSS.d-1)
MLSS (8 kg.m-3)
Nitrification occurs until 0.4 kg COD.kg-1 TSS.d-1 at moderate temperatures. Higher temperatures could allow nitrification even with higher loading rates.
=
Q Flow rate (m3.d-1)
COD COD concentration (kg.m-3)
V­reactor,bio Reactor volume (m3)

## Slide 46
Design volume
based on biological constraints
MAX. SLR (kg COD.kg-1 TSS.d-1)
is dependent on - wastewater temperature
- effluent requirements
65%
Reaction phase
SLR (kg COD.kg-1 TSS.d-1)
MLSS (8 kg.m-3)
Nitrification occurs until 0.4 kg COD.kg-1 TSS.d-1 at moderate temperatures. Higher temperatures could allow nitrification even with higher loading rates.
=
Q Flow rate (m3.d-1)
COD COD concentration (kg.m-3)
V­reactor,bio Reactor volume (m3)
MLSS Sludge concentration (8 kg.m-3)

## Slide 47
Design volume
based on biological constraints
MAX. SLR (kg COD.kg-1 TSS.d-1)
is dependent on - wastewater temperature
- effluent requirements
65%
Reaction phase
SLR (kg COD.kg-1 TSS.d-1)
MLSS (8 kg.m-3)
Nitrification occurs until 0.4 kg COD.kg-1 TSS.d-1 at moderate temperatures. Higher temperatures could allow nitrification even with higher loading rates.
=
Q Flow rate (m3.d-1)
COD COD concentration (kg.m-3)
V­reactor,bio Reactor volume (m3)
MLSS Sludge concentration (8 kg.m-3)
Total reaction time per day (h.d-1)
Number of reactors

## Slide 48
Design volume
based on biological constraints
Vreactor,bio =
V­reactor,bio Reactor volume (m3)
Q Flow rate (m3.d-1)
COD COD concentration (kg.m-3)
SLR Sludge loading rate (0.4 kg COD.kg-1 TSS.d-1)
for nitrification at moderate temperatures
MLSS Sludge concentration (8 kg.m-3)
Total reaction time per day (h.d-1)
Number of reactors
Reaction phase
SLR (kg COD.kg-1 TSS.d-1)
MLSS (8 kg/m3)

## Slide 49
Design volume
based on biological constraints
Vreactor,bio =
V­reactor,bio Reactor volume (m3)
Q Flow rate (m3.d-1)
COD COD concentration (kg.m-3)
SLR Sludge loading rate (0.4 kg COD.kg-1 TSS.d-1)
for nitrification at moderate temperatures
MLSS Sludge concentration (8 kg.m-3)
Total reaction time per day (h.d-1)
Number of reactors
Reaction phase
SLR (kg COD.kg-1 TSS.d-1)
MLSS (8 kg/m3)

## Slide 50
Design volume
based on biological constraints
Vreactor,bio =
V­reactor,bio Reactor volume (m3)
Q Flow rate (m3.d-1)
COD COD concentration (kg.m-3)
SLR Sludge loading rate (0.4 kg COD.kg-1 TSS.d-1)
for nitrification at moderate temperatures
MLSS Sludge concentration (8 kg.m-3)
Total reaction time per day (h.d-1)
Number of reactors
Reaction phase
SLR (kg COD.kg-1 TSS.d-1)
MLSS (8 kg/m3)
TO BE CALCULATED – NEXT SLIDES

## Slide 51
REACTION TIME
is based on

## Slide 52
REACTION TIME
is based on
  influent concentrations

## Slide 53
REACTION TIME
is based on
  influent concentrations
  VER

## Slide 54
REACTION TIME
is based on
  influent concentrations
  VER
  conversion rates (COD, N and P)

## Slide 55
REACTION TIME
is based on
  influent concentrations
  VER
  conversion rates (COD, N and P)
calculate numerically or
set based on experience

## Slide 56
REACTION TIME
is based on
  influent concentrations
  VER
  conversion rates (COD, N and P)
Reaction time per day
calculate numerically or
set based on experience

## Slide 57
REACTION TIME
is based on
  influent concentrations
  VER
  conversion rates (COD, N and P)
Reaction time per day
calculate numerically or
set based on experience

## Slide 58
REACTION TIME
is based on
  influent concentrations
  VER
  conversion rates (COD, N and P)
Reaction time per day
calculate numerically or
set based on experience

## Slide 59
FEEDING TIME
Length: typically, 1h

## Slide 60
FEEDING TIME
Length: typically, 1h
- set by the hydraulic constraints on the specific treatment site

## Slide 61
FEEDING TIME
Length: typically, 1h
- set by the hydraulic constraints on the specific treatment site
- dependent on the local ratios of COD/P, RBCOD/COD and the fraction of hydrolysable substrate to ensure enough RBCOD uptake

## Slide 62
Settling time

## Slide 63
Settling time
Length: typically, 15-30 min

## Slide 64
Settling time
Length: typically, 15-30 min
Fraction with low-settling velocity is removed by opening a valve at a certain height in the reactor at the end of the settling time

## Slide 65
Settling time
Length: typically, 15-30 min
Fraction with low-settling velocity is removed by opening a valve at a certain height in the reactor at the end of the settling time
Length of settling time determines the selection pressure based on settling velocity

## Slide 66
NUMBER OF REACTORS

## Slide 67
NUMBER OF REACTORS
Multiple reactors without buffer tank
to ensure the influent can be fed to one of the reactors at all times

## Slide 68
Design volume
Based on biological constraints
Vreactor,bio =
can now be calculated

## Slide 69
Overall design principle
Choose plant configuration
Calculate volume per reactor based on hydraulic and biological constraints
Choose limiting volume
Calculate reactor dimensions
Calculate buffer volume (if needed)
Calculate total plant volume

## Slide 70
Limiting volume
Based on hydraulic constraints
Based on biological constraints
Vreactor,bio =
Vreactor,hyd =
Vreactor = max(Vreactor,bio, Vreactor,bio)

## Slide 71
Overall design principle
Choose plant configuration
Calculate volume per reactor based on hydraulic and biological constraints
Choose limiting volume
Calculate reactor dimensions
Calculate buffer volume (if needed)
Calculate total plant volume

## Slide 72
Reactor dimensions
,

## Slide 73
Reactor dimensions
,
=

## Slide 74
Reactor dimensions
,
=
= ≤ 5 m.h-1
upflow velocity (m.h-1)

## Slide 75
Reactor dimensions
,
=
= ≤ 5 m.h-1
upflow velocity (m.h-1)
to prevent sludge washout (hydraulic constraint)

## Slide 76
Reactor dimensions
,
=
= ≤ 5 m.h-1
upflow velocity (m.h-1)
often restricted by
  construction costs and permits
  aeration system
to prevent sludge washout (hydraulic constraint)

## Slide 77
Overall design principle
Choose plant configuration
Calculate volume per reactor based on hydraulic and biological constraints
Choose limiting volume
Calculate reactor dimensions
Calculate buffer volume (if needed)
Calculate total plant volume

## Slide 78
BUFFER TANK VOLUME
= volume to be treated per cycle per reactor – volume treated per cycle per reactor

## Slide 79
BUFFER TANK VOLUME
= volume to be treated per cycle per reactor – volume treated per cycle per reactor
Qpeak DWF peak flow (m3.d-1)

## Slide 80
BUFFER TANK VOLUME
= volume to be treated per cycle per reactor – volume treated per cycle per reactor
Qpeak DWF peak flow (m3.d-1)

## Slide 81
BUFFER TANK VOLUME
= volume to be treated per cycle per reactor – volume treated per cycle per reactor
Qpeak DWF peak flow (m3.d-1)
This formula assumes that the buffer tank can be completely emptied during feeding

## Slide 82
BUFFER TANK VOLUME
= volume to be treated per cycle per reactor – volume treated per cycle per reactor
Qpeak DWF peak flow (m3.d-1)
This formula assumes that the buffer tank can be completely emptied during feeding
- Check it yourselves! See Example 11.3.3

## Slide 83: Effect of buffer tank
The application of a buffer does not lead immediately to a lower total volume
Notes: Matlab script:
%% given
Qpeak = 1000*24; % m3 d-1
Qdwf = 200*24; %m3 d-1
COD = 600*10^-3; %kg m-3
MLSS = 8; %kg MLSS m-3
SLR = 0.3; %kg COD/kg MLSS/d
Nreactors1 = 3; %reactors (without buffer),
Nreactors2 =2; %reactors (with buffer)
tsettle = 30/60; %h
treac = (60/60):0.1:(600/60);%h
%% calculation volume without buffer
tfeed = (treac + tsettle)./(Nreactors1-1); %h
t = tfeed + (treac + tsettle); %h
ncycles = 24./t;
treacd = ncycles.*treac; %h
V1 = (Qdwf.*COD)./((treacd./24).*MLSS.*SLR.*Nreactors1 ); %m3
V1tot = V1*Nreactors1; %m3
eff1 = treac./t.*100;
%% calculation volume with buffer
tfeed = 60/60; %h
t = tfeed + (treac + tsettle);%h
ncycles = 24./t;
treacd = ncycles.*treac; %h
Vbuffer = (Qdwf./(Nreactors2.*ncycles))-(Qdwf.*tfeed/24);%h
V2 = (Qdwf.*COD./(treacd./24.*MLSS.*SLR.*Nreactors2)); %m3
V2tot = (V2*Nreactors2)+Vbuffer; %m3
eff2 = treac./t.*100;
%% Figures
subplot(2,1,1)
plot(treac.*60, V1tot,treac.*60, V2tot)
legend('without buffer', 'with buffer')
xlim([0 600])
ylim([1600 3000])
subplot(2,1,2)
plot(treac.*60, eff1, treac.*60, eff2)
legend('without buffer', 'with buffer')
xlim([0 600])
ylim([40 100])

## Slide 84: Effect of buffer tank
The application of a buffer does not lead immediately to a lower total volume
nreactor, with buffer < nreactor, without buffer
Notes: Matlab script:
%% given
Qpeak = 1000*24; % m3 d-1
Qdwf = 200*24; %m3 d-1
COD = 600*10^-3; %kg m-3
MLSS = 8; %kg MLSS m-3
SLR = 0.3; %kg COD/kg MLSS/d
Nreactors1 = 3; %reactors (without buffer),
Nreactors2 =2; %reactors (with buffer)
tsettle = 30/60; %h
treac = (60/60):0.1:(600/60);%h
%% calculation volume without buffer
tfeed = (treac + tsettle)./(Nreactors1-1); %h
t = tfeed + (treac + tsettle); %h
ncycles = 24./t;
treacd = ncycles.*treac; %h
V1 = (Qdwf.*COD)./((treacd./24).*MLSS.*SLR.*Nreactors1 ); %m3
V1tot = V1*Nreactors1; %m3
eff1 = treac./t.*100;
%% calculation volume with buffer
tfeed = 60/60; %h
t = tfeed + (treac + tsettle);%h
ncycles = 24./t;
treacd = ncycles.*treac; %h
Vbuffer = (Qdwf./(Nreactors2.*ncycles))-(Qdwf.*tfeed/24);%h
V2 = (Qdwf.*COD./(treacd./24.*MLSS.*SLR.*Nreactors2)); %m3
V2tot = (V2*Nreactors2)+Vbuffer; %m3
eff2 = treac./t.*100;
%% Figures
subplot(2,1,1)
plot(treac.*60, V1tot,treac.*60, V2tot)
legend('without buffer', 'with buffer')
xlim([0 600])
ylim([1600 3000])
subplot(2,1,2)
plot(treac.*60, eff1, treac.*60, eff2)
legend('without buffer', 'with buffer')
xlim([0 600])
ylim([40 100])

## Slide 85: Effect of buffer tank
The application of a buffer does not lead immediately to a lower total volume
nreactor, with buffer < nreactor, without buffer
Vreactor, with buffer > Vreactor, without buffer
Notes: Matlab script:
%% given
Qpeak = 1000*24; % m3 d-1
Qdwf = 200*24; %m3 d-1
COD = 600*10^-3; %kg m-3
MLSS = 8; %kg MLSS m-3
SLR = 0.3; %kg COD/kg MLSS/d
Nreactors1 = 3; %reactors (without buffer),
Nreactors2 =2; %reactors (with buffer)
tsettle = 30/60; %h
treac = (60/60):0.1:(600/60);%h
%% calculation volume without buffer
tfeed = (treac + tsettle)./(Nreactors1-1); %h
t = tfeed + (treac + tsettle); %h
ncycles = 24./t;
treacd = ncycles.*treac; %h
V1 = (Qdwf.*COD)./((treacd./24).*MLSS.*SLR.*Nreactors1 ); %m3
V1tot = V1*Nreactors1; %m3
eff1 = treac./t.*100;
%% calculation volume with buffer
tfeed = 60/60; %h
t = tfeed + (treac + tsettle);%h
ncycles = 24./t;
treacd = ncycles.*treac; %h
Vbuffer = (Qdwf./(Nreactors2.*ncycles))-(Qdwf.*tfeed/24);%h
V2 = (Qdwf.*COD./(treacd./24.*MLSS.*SLR.*Nreactors2)); %m3
V2tot = (V2*Nreactors2)+Vbuffer; %m3
eff2 = treac./t.*100;
%% Figures
subplot(2,1,1)
plot(treac.*60, V1tot,treac.*60, V2tot)
legend('without buffer', 'with buffer')
xlim([0 600])
ylim([1600 3000])
subplot(2,1,2)
plot(treac.*60, eff1, treac.*60, eff2)
legend('without buffer', 'with buffer')
xlim([0 600])
ylim([40 100])

## Slide 86: Effect of buffer tank
The application of a buffer does not lead immediately to a lower total volume
nreactor, with buffer < nreactor, without buffer
Vreactor, with buffer > Vreactor, without buffer
, ,
Notes: Matlab script:
%% given
Qpeak = 1000*24; % m3 d-1
Qdwf = 200*24; %m3 d-1
COD = 600*10^-3; %kg m-3
MLSS = 8; %kg MLSS m-3
SLR = 0.3; %kg COD/kg MLSS/d
Nreactors1 = 3; %reactors (without buffer),
Nreactors2 =2; %reactors (with buffer)
tsettle = 30/60; %h
treac = (60/60):0.1:(600/60);%h
%% calculation volume without buffer
tfeed = (treac + tsettle)./(Nreactors1-1); %h
t = tfeed + (treac + tsettle); %h
ncycles = 24./t;
treacd = ncycles.*treac; %h
V1 = (Qdwf.*COD)./((treacd./24).*MLSS.*SLR.*Nreactors1 ); %m3
V1tot = V1*Nreactors1; %m3
eff1 = treac./t.*100;
%% calculation volume with buffer
tfeed = 60/60; %h
t = tfeed + (treac + tsettle);%h
ncycles = 24./t;
treacd = ncycles.*treac; %h
Vbuffer = (Qdwf./(Nreactors2.*ncycles))-(Qdwf.*tfeed/24);%h
V2 = (Qdwf.*COD./(treacd./24.*MLSS.*SLR.*Nreactors2)); %m3
V2tot = (V2*Nreactors2)+Vbuffer; %m3
eff2 = treac./t.*100;
%% Figures
subplot(2,1,1)
plot(treac.*60, V1tot,treac.*60, V2tot)
legend('without buffer', 'with buffer')
xlim([0 600])
ylim([1600 3000])
subplot(2,1,2)
plot(treac.*60, eff1, treac.*60, eff2)
legend('without buffer', 'with buffer')
xlim([0 600])
ylim([40 100])

## Slide 87: Effect of buffer tank
The application of a buffer does not lead immediately to a lower total volume
nreactor, with buffer < nreactor, without buffer
Vreactor, with buffer > Vreactor, without buffer
, ,
Vreactor, with buffer > Vreactor, without buffer
Notes: Matlab script:
%% given
Qpeak = 1000*24; % m3 d-1
Qdwf = 200*24; %m3 d-1
COD = 600*10^-3; %kg m-3
MLSS = 8; %kg MLSS m-3
SLR = 0.3; %kg COD/kg MLSS/d
Nreactors1 = 3; %reactors (without buffer),
Nreactors2 =2; %reactors (with buffer)
tsettle = 30/60; %h
treac = (60/60):0.1:(600/60);%h
%% calculation volume without buffer
tfeed = (treac + tsettle)./(Nreactors1-1); %h
t = tfeed + (treac + tsettle); %h
ncycles = 24./t;
treacd = ncycles.*treac; %h
V1 = (Qdwf.*COD)./((treacd./24).*MLSS.*SLR.*Nreactors1 ); %m3
V1tot = V1*Nreactors1; %m3
eff1 = treac./t.*100;
%% calculation volume with buffer
tfeed = 60/60; %h
t = tfeed + (treac + tsettle);%h
ncycles = 24./t;
treacd = ncycles.*treac; %h
Vbuffer = (Qdwf./(Nreactors2.*ncycles))-(Qdwf.*tfeed/24);%h
V2 = (Qdwf.*COD./(treacd./24.*MLSS.*SLR.*Nreactors2)); %m3
V2tot = (V2*Nreactors2)+Vbuffer; %m3
eff2 = treac./t.*100;
%% Figures
subplot(2,1,1)
plot(treac.*60, V1tot,treac.*60, V2tot)
legend('without buffer', 'with buffer')
xlim([0 600])
ylim([1600 3000])
subplot(2,1,2)
plot(treac.*60, eff1, treac.*60, eff2)
legend('without buffer', 'with buffer')
xlim([0 600])
ylim([40 100])

## Slide 88: Effect of buffer tank
The application of a buffer does not lead immediately to a lower total volume
nreactor, with buffer < nreactor, without buffer
Vreactor, with buffer > Vreactor, without buffer
, ,
Vreactor, with buffer > Vreactor, without buffer
- Check it yourselves! See Example 11.3.4
Notes: Matlab script:
%% given
Qpeak = 1000*24; % m3 d-1
Qdwf = 200*24; %m3 d-1
COD = 600*10^-3; %kg m-3
MLSS = 8; %kg MLSS m-3
SLR = 0.3; %kg COD/kg MLSS/d
Nreactors1 = 3; %reactors (without buffer),
Nreactors2 =2; %reactors (with buffer)
tsettle = 30/60; %h
treac = (60/60):0.1:(600/60);%h
%% calculation volume without buffer
tfeed = (treac + tsettle)./(Nreactors1-1); %h
t = tfeed + (treac + tsettle); %h
ncycles = 24./t;
treacd = ncycles.*treac; %h
V1 = (Qdwf.*COD)./((treacd./24).*MLSS.*SLR.*Nreactors1 ); %m3
V1tot = V1*Nreactors1; %m3
eff1 = treac./t.*100;
%% calculation volume with buffer
tfeed = 60/60; %h
t = tfeed + (treac + tsettle);%h
ncycles = 24./t;
treacd = ncycles.*treac; %h
Vbuffer = (Qdwf./(Nreactors2.*ncycles))-(Qdwf.*tfeed/24);%h
V2 = (Qdwf.*COD./(treacd./24.*MLSS.*SLR.*Nreactors2)); %m3
V2tot = (V2*Nreactors2)+Vbuffer; %m3
eff2 = treac./t.*100;
%% Figures
subplot(2,1,1)
plot(treac.*60, V1tot,treac.*60, V2tot)
legend('without buffer', 'with buffer')
xlim([0 600])
ylim([1600 3000])
subplot(2,1,2)
plot(treac.*60, eff1, treac.*60, eff2)
legend('without buffer', 'with buffer')
xlim([0 600])
ylim([40 100])

## Slide 89: Effect of buffer tank
The application of a buffer does increase the efficiency (= )

## Slide 90: Effect of buffer tank
The application of a buffer does increase the efficiency (= )
is fixed

## Slide 91: Effect of buffer tank
The application of a buffer does increase the efficiency (= )
is fixed
increases

## Slide 92: Effect of buffer tank
The application of a buffer does increase the efficiency (= )
is fixed
increases
(buffer) > (without buffer)

## Slide 93: Effect of buffer tank
The application of a buffer does increase the efficiency (= )
is fixed
increases
(buffer) > (without buffer)
- Check it yourselves! See Example 11.3.4

## Slide 94
Overall design principle
Choose plant configuration
Calculate volume per reactor based on hydraulic and biological constraints
Choose limiting volume
Calculate reactor dimensions
Calculate buffer volume (if needed)
Calculate total plant volume

## Slide 95
Total plant volume
Dependent on configuration:

## Slide 96
Total plant volume
Dependent on configuration:
Vplant = nreactor Vreactor

## Slide 97
Total plant volume
Dependent on configuration:
Vplant = Vbuffer + nreactor Vreactor

## Slide 98
Total plant volume
Dependent on configuration:
Vplant = Vbuffer + nreactor Vreactor + VC

## Slide 99
Summary ags design parameters
PHASE DURING BATCH OPERATION | DESIGN PARAMETER | DESIGN OUTCOME
Fill and draw phase | tfeed Q VER vup | Vreactor,hyd and Vreactor,bio Vreactor,hyd , Vreactor,bio ,Hreactor, Areactor and Vbuffer Vreactor,hyd Hreactor, Areactor
Reaction phase | treact SLR | Vreactor,bio Vreactor,bio
Settling phase | tsettling | Vreactor,bio

## Slide 100
Summary ags design parameters
PHASE DURING BATCH OPERATION | DESIGN PARAMETER | DESIGN OUTCOME
Fill and draw phase | tfeed Q VER vup | Vreactor,hyd and Vreactor,bio Vreactor,hyd , Vreactor,bio ,Hreactor, Areactor and Vbuffer Vreactor,hyd Hreactor, Areactor
Reaction phase | treact SLR | Vreactor,bio Vreactor,bio
Settling phase | tsettling | Vreactor,bio

## Slide 101
Summary ags design parameters
PHASE DURING BATCH OPERATION | DESIGN PARAMETER | DESIGN OUTCOME
Fill and draw phase | tfeed Q VER vup | Vreactor,hyd and Vreactor,bio Vreactor,hyd , Vreactor,bio ,Hreactor, Areactor and Vbuffer Vreactor,hyd Hreactor, Areactor
Reaction phase | treact SLR | Vreactor,bio Vreactor,bio
Settling phase | tsettling | Vreactor,bio
Don’t forget batch scheduling!

## Slide 102
conclusions - design of an ags plant

## Slide 103
conclusions - design of an ags plant
Follow the 6-step design procedure

## Slide 104
conclusions - design of an ags plant
Follow the 6-step design procedure
Volume is constrained by hydraulics and biology

## Slide 105
conclusions - design of an ags plant
Follow the 6-step design procedure
Volume is constrained by hydraulics and biology
Design should comply with both dry weather and rain weather conditions

## Slide 106
conclusions - design of an ags plant
Follow the 6-step design procedure
Volume is constrained by hydraulics and biology
Design should comply with both dry weather and rain weather conditions
The design procedure is an iterative process
to find an optimal design which is case-specific

## Slide 107
conclusions - design of an ags plant
Follow the 6-step design procedure
Volume is constrained by hydraulics and biology
Design should comply with both dry weather and rain weather conditions
The design procedure is an iterative process
to find an optimal design which is case-specific
Let’s apply this knowledge on the examples and exercises in