## Slide 1
Course on Membrane Bioreactors
Membrane Separation Principles
Xia Huang
Notes: Hello everyone! I’m Professor Xia Huang from Tsinghua University. In this chapter, we are going to have a look at membrane bioreactors and its applications, which could help you build a clear impression on this widely-applied technology in both municipal and industrial wastewater treatment processes.
Firstly we are going to learn section of Membrane separation principles

## Slide 2
Membrane separation
  Major function
    Separation
    Purification
    Concentration
  Selective permeable membrane
  Mechanisms
    Size sieving
    Diffusion/Electrodialysis
    Osmosis
    Phase transition
    …
  Key: selective permeable membrane
  Pores
  Driving force
  Pressure gradient
  Concentration gradient
  Temperature gradient
  Electric potential gradient
  …
Biological Wastewater Treatment
Online Course Series
Notes: The major function of membrane separation is to separate, purify or concentrate components from a mixture.
The key of membrane separation processes is the selective permeable membranes with special pores. By applying one or more driving forces across a selective permeable membrane, the designated components can preferentially penetrate the membrane.
The mechanisms of membrane separation include size sieving, diffusion/ electrodialysis, osmosis, phase transition, etc. Size sieving is a mechanical filtration process using porous membranes, while other mechanisms rely on the physicochemical interaction between the permeating components and membrane material. Membrane separation processes can be driven by pressure gradient, concentration gradient, temperature gradient, electric potential gradient, etc.

## Slide 3
  Pressure-driven membrane processes
    Microfiltration (MF): > 0.1 μm
    Ultrafiltration (UF): 0.002-0.100 μm
    (The rejectability is measured by
    Molecular weight cut-off)
    Nanofiltration (NF): 100-1,000 Dalton and some hardness ions
    Reverse osmosis (RO): salts and small size solutes
Pressure-driven processes
Biological Wastewater Treatment
Online Course Series
Notes: Pressure-driven membrane processes have been successfully applied in water purification, wastewater treatment, and water reclamation.
Microfiltration, ultrafiltration, nanofiltration, and reverse osmosis are the best examples. These four technologies are also called as their abbreviations: MF, UF, NF and RO.
The pore sizes of these membranes, in comparison with the particulate/ colloidal/soluble pollutant sizes in water, are schematically shown in the slide. As you can see, MF rejects particulate substances with a size larger than 0.1 μm, while UF rejects colloids and macromolecules with a size of 0.002-0.100 μm or more.
The rejectability of UF membranes is usually measured by molecular weight cut-off.
NF rejects organic compounds with a molecular weight of 100-1,000 Da or more as well as some hardness ions. RO rejects salts and small-size solutes in the feed mixture.
MF and UF are referred to as low-pressure processes, while NF and RO are referred to as high-pressure processes.

## Slide 4
Filtered effluent
Influent
Mixed liquor
Suction pump
Membrane Bioreactor (MBR):
Combination of biological treatment and membrane separation
Effluent
Membrane module
  MF or UF membranes are used in MBR
  High-quality effluent
  Independent control of sludge- and hydraulic retention time
  Longer sludge retention time
  Higher sludge concentration
How does the MBR work?
Biological Wastewater Treatment
Online Course Series
Notes: The membrane bioreactor, usually called as MBR, is a combination of biological treatment and membrane separation process. Instead of a conventional secondary sedimentation tank, MF or UF membranes are used to separate the treated effluent from the activated sludge solids.
The major purpose of MBR is exactly separating water from the activated sludge solids, and thus guarantee the effluent quality. With a high separation efficiency, the MBR can produce a clarified, high-quality effluent.
It also has other advantages, such as allowing the independent parameter control of sludge- and hydraulic retention time. These variables are normally linked in the conventional treatment processes.

## Slide 5
Liquid phase
Influent
Mixed liquor
particles and macromolecules
water and small molecules
Inner surface
External filtration surface
Effluent
Suction pump
Membrane module
Pressure difference
∆p>0
Hollow fiber membrane
Membrane tank
Membrane pores
∆p>0
How does the MBR work?
Biological Wastewater Treatment
Online Course Series
Notes: So, how does a MBR work? Let’s take a submerged MBR with hollow fiber membrane modules as an example.
As you can see in the illustration, the pump suction to the membrane modules creates a net negative pressure inside the hollow fiber lumen, resulting in a pressure difference between the inside and the outside of the membrane.
The pressure difference p forces water and small molecules to pass through the membrane pores, forming effluent, while larger particulate biomass flocs and macromolecules are rejected.

## Slide 6
  Retained matters
  Sludge flocs
  Bacteria cells
  Colloids (partial)
  Soluble biopolymers (partial)
Liquid phase
Influent
Mixed liquor
particles and macromolecules
water and small molecules
Effluent
Suction pump
Membrane module
Pressure difference
∆p>0
Hollow fiber membrane
Membrane tank
How does the MBR work?
Biological Wastewater Treatment
Online Course Series
Notes: In this way, a full portion of sludge flocs and bacteria cells, and some of the colloidal and soluble biopolymers in the sludge could be retained by the membrane, thus producing effluent with high quality.