## Slide 1
Course on Membrane Bioreactors
Practical Applications
- Part 2
Hector A. Garcia

## Slide 2: Contents
  Introduction
  High-loaded MBR
  Oxygen transfer limitations
  Alternatives technologies for oxygen transfer
  SDOX system
  Speece cone system
  SDOX application
  Speece cone application
Biological Wastewater Treatment
Online Course Series
Latest Developments in MBR Systems

## Slide 3: Introduction
Biological Wastewater Treatment
Online Course Series
Sludge
Sludge
Primary
Sedimentation
Secondary
Sedimentation
Activated
Sludge
Preliminary
Treatment
To
Tertiary
Treatment
Thickening
Digestion
Dewatering
Water Recycle
to Head of Plant
Sludge to
Land Disposal
Water Recycle
to Head of Plant

## Slide 4: Introduction
Biological Wastewater Treatment
Online Course Series
Sludge
Sludge
Primary
Sedimentation
Secondary
Sedimentation
Activated
Sludge
Preliminary
Treatment
To
Tertiary
Treatment
Thickening
Digestion
Dewatering
Water Recycle
to Head of Plant
Sludge to
Land Disposal
Water Recycle
to Head of Plant

## Slide 5: Introduction
Biological Wastewater Treatment
Online Course Series
  large footprint
  two or three stage process
  settlement problems from “bulking”
  further polishing required for disinfection/clarification
  equalisation of hydraulic and organic loadings required
  .. so, all OK then – as long as you:
  have enough land, and
  don’t want to recycle
Conventional Systems

## Slide 6: Introduction
Biological Wastewater Treatment
Online Course Series
Effluent
Sludge waste
Influent
Air

## Slide 7: Introduction
Biological Wastewater Treatment
Online Course Series
Effluent
Influent
Air

## Slide 8: Introduction
Biological Wastewater Treatment
Online Course Series
Effluent
Influent
Air

## Slide 9: Introduction
Biological Wastewater Treatment
Online Course Series
  An MBR combines aerobic biotreatment with membrane separation, thus:
  Clarified, disinfected effluent. Low turbidity, bacteria, TSS and organic content
  Small footprint plant. Shorter HRT (V/Q)
  Bulking problems become less relevant. Longer SRTs with less sludge production
  Hydraulic and solids retention time are uncoupled
  Intensive biotreatment provided, esp. nitrification
  .. all of which means MBRs are:
  capable of meeting stringent environmental standards
  KEY CANDIDATE WASTEWATER RECYCLING TECHNOLOGY

## Slide 10: High-loaded MBR
Biological Wastewater Treatment
Online Course Series
  Operating at high MLSS introduces advantages:
  Receiving higher influent wastewater loading rates (using the existing facilities)
  Reducing the footprint requirements
  Operating at larger solid retention time (SRT) conditions
  Among commercially available technologies MBRs are arguably the most suitable technology to operate at high MLSS concentrations; the operation of MBR systems is not affected by the settling characteristics of the sludge.

## Slide 11: High-loaded MBR
Biological Wastewater Treatment
Online Course Series
  Advantages of innovative MBR operated at high MLSS 15 to 40 g L-1 (high-loaded MBR – HLMBR):
  Increased capacity to treat higher organic loading rates
  Increased oxygen uptake rates (OURs) linked a higher chemical oxygen demand (COD) conversion rate
  Minimized footprint - reducing volume needs and construction costs
  Reduced waste solids handling costs
  Encourage the design of compact/containerized movable/portable MBRs for municipal/industrial wastewater in remote areas without access to sewers.
  Ideal for on-site/decentralized alternatives for the provision of urgent services in the context of emergency sanitation

## Slide 12: High-loaded MBR
Biological Wastewater Treatment
Online Course Series
  HL-MBR conditions can be accomplished by either:
  (i) Operating the MBR system at high SRT conditions (i.e., not wasting sludge). Produces little fully digested sludge; MLSS consists of non-biodegradable and inorganic suspended solids instead of active biomass without enhancing the treatment capacity of the system at a given footprint.
  (ii) working at high influent loading rate. Operating at low SRTs (5-15 days) and high influent loading rate result in active biomass. Treatment capacity enhanced reducing footprint at a given loading rate, or alternatively, for a given footprint increasing the loading rate treatment capacity.

## Slide 13: High-loaded MBR
Biological Wastewater Treatment
Online Course Series
Design advantages of a HL-MBR as a function of the MLSS concentration without considering oxygen transfer inefficiencies introduced by bubble diffusers (adapted from Kim et al., (2019))
SRT = 10 days

## Slide 14: High-loaded MBR
Biological Wastewater Treatment
Online Course Series

## Slide 15: Oxygen transfer limitations
Biological Wastewater Treatment
Online Course Series
  Poor/negligible oxygen transfer when using conventional aeration (fine/coarse bubble diffusers); even lower performance when introducing oxygen in process water; aeration can represent up to 75% of the total operational cost
  Effects of MLSS on the oxygen transfer = alpha factor (mass transfer ratio of process-water to clean-water).
  Alpha factor exponentially decreased with MLSS concentration, even reaching certain MLSS at which negligible alpha factors are reported.
  The oxygen transfer proportional to the SRT; the lower the SRT, the lower the oxygen transfer efficiency and the alpha factor.
  Therefore, the design features of the HL-MBR concept (high MLSS concentration and low SRT) maximizes the oxygen transfer limitations inherent of conventional diffused aeration systems.

## Slide 16: Oxygen transfer limitations
Biological Wastewater Treatment
Online Course Series
Figure 2.13 © IWA Publishing 2018. Aeration, Mixing, and Energy: Bubbles and Sparks; Editor: Diego Rosso; doi:10.2166/9781780407845_0031

## Slide 17: Oxygen transfer limitations
Biological Wastewater Treatment
Online Course Series

## Slide 18: Alternatives technologies
Biological Wastewater Treatment
Online Course Series
  Non-conventional aeration technologies proposed to enhance the oxygen transfer process: a) Deep-shaft (U-Tube contactor or vertical shaft); b) High purity oxygen (HPO) aeration system; and c) Supersaturated oxygen aeration systems
  Systems rely on increasing the amount of DO in the liquid phase by increased the partial pressure of oxygen in the gas phase.
  Disadvantages include high capital, operation, and maintenance costs.
  Supersaturated oxygen aeration systems work with HPO and at high-pressure conditions achieving higher OTRs.
  The two most relevant supersaturated oxygen aeration technologies include the supersaturated dissolved oxygen (SDOX) system and the Speece cone technology.

## Slide 19: SDOX System
Biological Wastewater Treatment
Online Course Series
  Novel alternative developed by BlueInGreen, LLC in USA
  Pressurized chamber operated at high pressure conditions (800 kPa) connected to an HPO source.
  A stream of the solution to be oxygenated is recirculated through the pressurized chamber where it gets in contact with the HPO at the high-pressure conditions in the chamber
  The influent streams enters at the top of the pressurized chamber where a large gas-liquid interface is created between the liquid and pure oxygen.
  Under pressure, the oxygen is quickly and efficiently dissolved into the solution.

## Slide 20: SDOX System
Biological Wastewater Treatment
Online Course Series
  The oxygen-supersaturated stream is returned back to the receiving basin through specially designed distribution pipes.
  The high pressure conditions exerted in the pressurized chamber allows reaching DO concentrations of up to 350 mg L-1, higher than other technologies.
  OTEs higher than 95% have been reported for the SDOX system
  The SDOX technology has been mostly evaluated for introducing DO in the context of lake and river restoration; other application includes the odour control in municipal sewer systems.

## Slide 21: SDOX System
Biological Wastewater Treatment
Online Course Series

## Slide 22: Speece Cone System
Biological Wastewater Treatment
Online Course Series
  Developed by Dr. Richard Speece in 1971.
  Down flow conical bubble contact chamber connected to a HPO source.
  A stream of the solution to be oxygenated is introduced on the top of the Speece cone chamber at a given flowrate and at a moderate pressure; an HPO flow is simultaneously introduced at the top of the cone.
  The oxygen-rich supersaturated solution is then returned back into the receiving basin through submerged diffusers.

## Slide 23: Speece Cone System
Biological Wastewater Treatment
Online Course Series
  The downward water velocity in the conical contact chamber should be high enough (higher than the gas buoyance of the gas) to push the oxygen bubbles down in the cone, but not too high to avoid the oxygen bubbles to escape the system undissolved.
  The Speece cone technology has been mostly applied for introducing DO aiming at lake and river restoration. Other applications include sulphide oxidation and sewer odour control.

## Slide 24: Speece Cone System
Biological Wastewater Treatment
Online Course Series

## Slide 25: Alternatives technologies
Biological Wastewater Treatment
Online Course Series
  Supersaturated oxygen aeration systems show several advantages:
  Lower operational cost considering both their simple operation and maintenance needs, as well as their excellent reported OTE values of above 95%
  Not affected by the submergence of the system.
  Systems are fully movable/portable ideally for coupling with movable/portable wastewater treatment systems.
  Very simple and easy to up-scale, so a big advantage for retrofitting wastewater treatment systems.
  If the supersaturated oxygen aeration technologies can effectively and efficiently supply DO into high MLSS concentrations, the limitations imposed by conventional diffused aeration for working at high MLSS concentrations may be uncapped.

## Slide 26: SDOX Application
Biological Wastewater Treatment
Online Course Series
  The oxygen transfer performance of the SDOX system at the high MLSS concentration range (4 to 40 g L-1) in the context of the HL-MBR concept was evaluated by Kim et al. (2020). The authors evaluated the oxygen mass transfer rate coefficient (KLa), the standard oxygen transfer rate (SOTR), the SOTE and the alpha factors. Moreover, the energy requirement of the SDOX system as a function of the MLSS concentrations were also discussed.

## Slide 27: SDOX Application
Biological Wastewater Treatment
Online Course Series

## Slide 28: SDOX Application
Biological Wastewater Treatment
Online Course Series

## Slide 29: SDOX Application
Biological Wastewater Treatment
Online Course Series

## Slide 30: SDOX Application
Biological Wastewater Treatment
Online Course Series

## Slide 31: Speece Cone Application
Biological Wastewater Treatment
Online Course Series

## Slide 32: Speece Cone Application
Biological Wastewater Treatment
Online Course Series

## Slide 33: Speece Cone Application
Biological Wastewater Treatment
Online Course Series

## Slide 34: Speece Cone Application
Biological Wastewater Treatment
Online Course Series
  Moreover, (not shown in that figure), the higher the HPO flowrate, the lower the SOTE (both in clean water and in sludge).
  Therefore, the decision at which HPO gas flowrate to operate when the system is operated with sludge also have a strong impact on the operational cost, since the SOTE is even more affected than when working with clean water.
  Still SOTE values approximate to 100% can be achieved when operating with sludge, but at the expenses of either having a much bigger Speece cone system, or by operating at a much higher sludge recirculation rates through the Speece cone (i.e. higher energy needs and operational costs).
  Much higher SOTE values (up to a maximum of 96%) were obtained compared to conventional diffused aeration; even for the lowest SOTE reported in this study.

## Slide 35: Speece Cone Application
Biological Wastewater Treatment
Online Course Series
  Compared to fine bubble diffused aeration, the Speece cone is more efficient, since nearly 100% of the supplied oxygen can be effectively delivered into the final receiving solution.
  Moreover, without the needs for the large amount of energy that is necessary to compress tremendous amounts of air in diffused aeration systems that is released back in the atmosphere carrying several volatile compounds.
  In addition, the Speece cone may also be free of maintenance, since it does not require diffusers cleaning nor replacement.

## Slide 36: Speece Cone Application
Biological Wastewater Treatment
Online Course Series