## Slide 1
Course on Membrane Bioreactors
Wastewater Treatment
Performance and
Effluent Quality
Shuai Liang
Notes: Hello everyone! I’m Professor Shuai Liang at Beijing Forestry University. Today, we’re going to learn about the wastewater treatment performance and effluent quality of the MBRs. ########

## Slide 2: Contents
  Ordinary pollutant removal
  Hygiene water quality
  Emerging pollutant removal
  Energy recovery
Biological Wastewater Treatment
Online Course Series
Notes: In this section, we will first learn about the removal performance of MBRs for ordinary pollutants. Then we will learn about the hygiene water qualities of the MBR effluent, where we will know the unique advantages of the MBRs in removing pathogenic microorganisms. Then we will learn about the removal performance of the MBRs for emerging pollutants. At last, we will learn about the development potential of MBRs in energy recovery.

## Slide 3: Ordinary pollutant removal
Organic matter
(COD/BOD)
Ammonium nitrogen
(NH4+-N)
Total nitrogen
(TN)
Total phosphorus
(TP)
Suspended solids
(SS)
Turbidity
Ordinary pollutant
Ordinary pollutant composition
  Wastewater type
  e.g. municipal vs. industrial
  Effluent demand
  e.g. discharge vs. reuse
  Different specific standards
Treatment efficiency requirement
Biological Wastewater Treatment
Online Course Series
Notes: First is about the ordinary pollutant removal by MBRs. ######## The ordinary pollutants typically include organic matter, ammonium nitrogen (NH4+-N), total nitrogen (TN), total phosphorus (TP), suspended solids (SS), and turbidity. The organic matter was usually quantified in terms of chemical oxygen demand, short for COD, or biological oxygen demand, short for BOD. ########The required treatment efficiency for these pollutants is usually different, depending on the influent wastewater type, effluent demand, and the corresponding specific treatment standards. For example, the treatment efficiency required for municipal wastewater and industrial wastewater can be different. Besides, the treatment standards will be much higher if the wastewater is treated for reuse purpose than for discharge purpose. And also, the specific treatment standards adopted in different countries are different, that will lead to different treatment requirement.

## Slide 4: Ordinary pollutant removal
TN removal
  The AAO-MBR process is the most prevalent process in large-scale MBR-based plants for municipal wastewater treatment.
MBR process development
AAO-MBR
AO-MBR
O-MBR
T and P removal
Biological Wastewater Treatment
Online Course Series
Notes: There are many different configurations of the MBR process. ######## The primary version of MBR is a simple combination of the aerobic unit and membrane tank, it can be named as O-MBR, and it can be used to effectively remove COD, BOD, Ammonia nitrogen, and SS. The first wave of full-scale MBRs, which were established in the 1990s or 2000s, were mainly in the form of O-MBR. ########For the total nitrogen removal, denitrification is required and, therefore, an anoxic zone should be added before or after the aerobic tank, that forms an anoxic/aerobic-MBR process, which can be named as AO-MBR. ########For simultaneous removal of the N and P nutrients using a biological method, an anaerobic zone is further added to trigger the microbial phosphorus release-and-uptake mechanism and forms an anaerobic/anoxic/aerobic-MBR process, which can be named as AAO-MBR. ######## The AAO-MBR process is the most prevalent process in large-scale MBR-based plants for municipal wastewater treatment. By the way, the detailed arrangement of the zones can differ according to the specific design of the process flow.

## Slide 5: Ordinary pollutant removal
  The influent concentrations of COD, NH4+-N, TN, and TP were mainly in the ranges of 500-700, 25-50, 40-70, and 6-12 mg/L, respectively.
Influent quality
Effluent quality
Removal efficiency
Situation of COD, NH4+-N, TN, and TP in full‐scale MBRs treating municipal wastewater
Municipal wastewater treatment
Biological Wastewater Treatment
Online Course Series
Notes: For municipal wastewater treatment, a literature survey of the treatment efficiencies of COD, ammonium nitrogen, total nitrogen, and Total phosphorus in full-scale municipal wastewater MBRs is given in these Figures. ######## We can see the survey shows that the influent concentrations of COD, ammonium nitrogen, total nitrogen, and Total phosphorus were mainly in the ranges of 500-700, 25-50, 40-70, and 6-12 mg/L, respectively.

## Slide 6: Ordinary pollutant removal
  The effluent concentrations of COD, NH4+-N, TN, and TP were mainly in the ranges of 10-30, 0-3, 5-15, and 0-1 mg/L, respectively.
Influent quality
Effluent quality
Removal efficiency
Situation of COD, NH4+-N, TN, and TP in full‐scale MBRs treating municipal wastewater
Municipal wastewater treatment
Biological Wastewater Treatment
Online Course Series
Notes: The effluent concentrations of COD, ammonium nitrogen, total nitrogen, and Total phosphorus were mainly in the ranges of 10-30, 0-3, 5-15, and 0-1 mg/L, respectively.

## Slide 7: Ordinary pollutant removal
  Average removal rate of COD, and NH4+-N : ~ 95%
  TN removal rate mostly reached 80-90%
  TP removal rate varied from 80% to 99% (mainly 87-98%)
Influent quality
Effluent quality
Removal efficiency
Situation of COD, NH4+-N, TN, and TP in full‐scale MBRs treating municipal wastewater
Municipal wastewater treatment
Biological Wastewater Treatment
Online Course Series
Notes: An average rate of ~95% was achieved for COD and ammonium nitrogen removal. Although with a larger fluctuation, the total nitrogen removal rate mostly reached 80%-90%. The Total phosphorus removal rate varied from 80% to 99% (mainly in the 87%-98% range), depending on the biological status and chemical dosages into the process for Total phosphorus removal.

## Slide 8: Ordinary pollutant removal
  MBR is particularly effective in the removal of SS, COD, and NH4+-N
  MBR is also competitive for TN removal
  MBR requires chemical precipitation to further remove TP
  CAS vs. MBR
Influent quality
Effluent quality
Removal efficiency
Situation of COD, NH4+-N, TN, and TP in full‐scale MBRs treating municipal wastewater
Municipal wastewater treatment
Biological Wastewater Treatment
Online Course Series
Notes: Compared with COVENTIONAL ACTIVATED SLUDGE processes, MBR is particularly effective in the removal of SS, COD, and ammonium nitrogen. As for biological nutrient removal (BNR), MBR is also competitive for total nitrogen removal. But for Total phosphorus, chemical precipitation is sometimes required to assist in further removal of Total phosphorus. Overall, we can see that the MBR process is extremely suitable for municipal wastewater treatment.

## Slide 9: Ordinary pollutant removal
Industrial wastewaters treatment
Representative large-scale MBR projects for industrial wastewater treatment in China since 2015
  An increasing number of MBRs have been applied to treat a variety of industrial wastewaters.
  The pollutant removal efficiencies vary largely according to the wastewater type
Biological Wastewater Treatment
Online Course Series
Notes: The application of MBR has also been extended to industrial wastewater treatment. This table shows the representative large-scale MBR projects for industrial wastewaters treatment in China since 2015. ######## An increasing number of MBRs have been applied to treat a variety of industrial wastewaters. The pollutant removal efficiencies vary largely according to the wastewater type.

## Slide 10: Ordinary pollutant removal
Zhang J., Xiao K. and Huang X. (2020). Full-scale MBR applications for leachate treatment in China: Practical, technical, and economic features. Journal of Hazardous Materials, 389, 122138
Full-scale leachate treatment
  A recent survey shows that MBR units can achieve:
  over 90% of BOD and COD removal
  95% of NH4+-N removal
The application of full-scale MBRs for leachate treatment in China
(the MBRs were with individual treatment capacity of ≥100 m3/d)
Biological Wastewater Treatment
Online Course Series
Notes: MBR has even been applied for full-scale leachate treatment. ######## As we can see in this figure, the capacity of full-scale MBRs for leachate treatment in China has been increasing and ######## a recent survey shows that MBR units can achieve more than 90% of BOD and COD removal and over 95% of ammonium nitrogen removal. Further research and development are definitely worthwhile.

## Slide 11: Ordinary pollutant removal
Ordinary pollutant removal mechanisms: Direct rejection
  Directly rejecting sludge flocs, microorganism cells, and other suspended solids larger than 0.5 µm.
Membrane
Microorganism
Sludge flocs
Colloids
Solutes
  Enhanced capability
  of membrane rejection
Schematic of membrane rejection process
  Enabling partial rejection of biopolymer clusters and debris, colloidal COD/N/P, and soluble substances.
Membrane
Cake layer
Biological Wastewater Treatment
Online Course Series
Notes: There are several technical advances of MBR to support its excellence in ordinary pollutant removal, ######## and that correspond to different removal mechanisms. Firstly, these membranes can directly reject sludge flocs, microorganism cells, and other suspended solids larger than 0.5 µm. ######## Besides, after a certain operation period, the membrane pores will be narrowed due to adsorption/blocking of foulants or the membrane surface is covered by a dynamic foulant layer, these consequently can enhance the rejection ability of the membranes, thereby enabling the partial rejection of biopolymer clusters and debris, colloidal COD/N/P, and even soluble substances such as SMP and some less biodegradable solutes.

## Slide 12: Ordinary pollutant removal
Ordinary pollutant removal mechanisms: Enhancing the biological process
Membrane
Bacteria
Sludge flocs
Colloids
Solutes
Biological Wastewater Treatment
Online Course Series
Notes: We know that the microfiltration or ultrafiltration process is a physical process, and it is not likely to straightforwardly change the nature of the microorganisms in the MBR tanks. However, it can profoundly enhance the biological process due to complete retention of the microorganisms and partial rejection of the pollutants.
The complete separation of Hydraulic Retention Time (HRT) and Sludge Retention Time (SRT) enables MBR to maintain a high######## sludge concentration and a low food-to-microorganism (F/M) ratio. That means the sludge loading is lower in MBRs. Therefore, ######## the microorganisms can be more readily kept in the endogenous /ɛn'dɑdʒənəs/ respiratory /ˈrespərətɔːri/ period for more thorough degradation of the pollutants. ######## For municipal wastewater treatment, the sludge loading of MBR is typically in the ######## range of 0.03-0.10 kgBOD5/kgMLSS.d. This is lower than that of Conventional Activated Sludge, which is ######## normally 0.05-0.15 kgBOD5/kgMLSS.d. Moreover, ######## the co-retention of microorganisms and pollutants is also conducive to microbial co-metabolism /məˈtæbəlɪzəm/ for the removal of refractory pollutants. Again, due to membrane rejection, nitrifying bacteria are easier to enrich in the system and become more resilient at low temperatures, which is important to the stable removal of ammonium nitrogen and beneficial for overall total nitrogen removal.

## Slide 13: Ordinary pollutant removal
Ordinary pollutant removal mechanisms: Enhancing the biological process
  Complete separation of HRT and SRT
    High sludge concentration
    Low F/M ratio
    More thorough degradation of the pollutants
  Conducive to microbial co-metabolism for the removal of refractory pollutants
  Stable removal of NH4+-N, beneficial for overall TN removal
Membrane
Sludge flocs
Colloids
Solutes
Biological Wastewater Treatment
Online Course Series
HRT: Hydraulic retention time; SRT: Sludge retention time; F/M: Food-to-microorganism ratio.
Bacteria
Notes: We know that the microfiltration or ultrafiltration process is a physical process, and it is not likely to straightforwardly change the nature of the microorganisms in the MBR tanks. However, it can profoundly enhance the biological process due to complete retention of the microorganisms and partial rejection of the pollutants.
The complete separation of Hydraulic Retention Time (HRT) and Sludge Retention Time (SRT) enables MBR to maintain a high######## sludge concentration and a low food-to-microorganism (F/M) ratio. That means the sludge loading is lower in MBRs. Therefore, ######## the microorganisms can be more readily kept in the endogenous /ɛn'dɑdʒənəs/ respiratory /ˈrespərətɔːri/ period for more thorough degradation of the pollutants. ######## For municipal wastewater treatment, the sludge loading of MBR is typically in the ######## range of 0.03-0.10 kgBOD5/kgMLSS.d. This is lower than that of Conventional Activated Sludge, which is ######## normally 0.05-0.15 kgBOD5/kgMLSS.d. Moreover, ######## the co-retention of microorganisms and pollutants is also conducive to microbial co-metabolism /məˈtæbəlɪzəm/ for the removal of refractory pollutants. Again, due to membrane rejection, nitrifying bacteria are easier to enrich in the system and become more resilient at low temperatures, which is important to the stable removal of ammonium nitrogen and beneficial for overall total nitrogen removal.

## Slide 14: Ordinary pollutant removal
Ordinary pollutant removal mechanisms: Enhancing the biological process
  Complete separation of HRT and SRT
    High sludge concentration
    Low F/M ratio
    More thorough degradation of the pollutants
  Conducive to microbial co-metabolism for the removal of refractory pollutants
  Stable removal of NH4+-N, beneficial for overall TN removal
Membrane
Bacteria
Sludge flocs
Colloids
Solutes
Biological Wastewater Treatment
Online Course Series
  Sludge
  loading
  CAS vs MBR
  0.03 - 0.10
  0.05 - 0.15
  Unit: kgBOD5/kgMLSS.d
Notes: We know that the microfiltration or ultrafiltration process is a physical process, and it is not likely to straightforwardly change the nature of the microorganisms in the MBR tanks. However, it can profoundly enhance the biological process due to complete retention of the microorganisms and partial rejection of the pollutants.
The complete separation of Hydraulic Retention Time (HRT) and Sludge Retention Time (SRT) enables MBR to maintain a high######## sludge concentration and a low food-to-microorganism (F/M) ratio. That means the sludge loading is lower in MBRs. Therefore, ######## the microorganisms can be more readily kept in the endogenous /ɛn'dɑdʒənəs/ respiratory /ˈrespərətɔːri/ period for more thorough degradation of the pollutants. ######## For municipal wastewater treatment, the sludge loading of MBR is typically in the ######## range of 0.03-0.10 kgBOD5/kgMLSS.d. This is lower than that of Conventional Activated Sludge, which is ######## normally 0.05-0.15 kgBOD5/kgMLSS.d. Moreover, ######## the co-retention of microorganisms and pollutants is also conducive to microbial co-metabolism /məˈtæbəlɪzəm/ for the removal of refractory pollutants. Again, due to membrane rejection, nitrifying bacteria are easier to enrich in the system and become more resilient at low temperatures, which is important to the stable removal of ammonium nitrogen and beneficial for overall total nitrogen removal.

## Slide 15: Ordinary pollutant removal
Ordinary pollutant removal mechanisms: Biological P removal
  High sludge concentration
  High P concentration in the sludge phase
  Rejecting some of the colloidal P
  Longer SRT (15-30 d), slower discharge of excess sludge
  Sometimes chemical removal of TP is required
Adding precipitants or coagulants has the merit of alleviating membrane fouling
Biological Wastewater Treatment
Online Course Series
Notes: For biological P removal, MBR acts like a double- edged sword. ######## On the one hand, MBR can possess a high sludge concentration and a high P content per unit mass of sludge and the membrane can reject some of the colloidal P as well; ######## on the other hand, the typically longer Sludge Retention Time (SRT) (15-30 d) of MBR means a slower discharge of the excess sludge from the system. And chemical removal of Total phosphorus (by adding precipitants or coagulants) is sometimes needed to guarantee the effluent quality. ######## It is noteworthy that adding precipitants or coagulants also has the merit of alleviating membrane fouling

## Slide 16: Ordinary pollutant removal
Operation and modularized installation
  More resistant to sludge bulking problems
  More stable operation and pollutant removal under unstable conditions
  Easier for modularized installation, more convenient for automatic operation
  Wider application areas
Schematic of modularized installation of MBRs
Biological Wastewater Treatment
Online Course Series
Notes: From the Operation perspective########, due to the complete rejection of biomass by the membrane, the MBR system is more resistant to the sludge bulking problems which usually trouble the Conventional Activated Sludge processes. In addition, the microorganisms in the MBR are more adaptable in unstable environments. Compared with the Conventional Activated Sludge process, a more stable operation and pollutant removal may be achieved by MBR in cases of high-strength wastewater, frequent shock of influent quality, fragile microbiota /ˌmaikrəubai'əutə/, or unstable ambient conditions.
Moreover, MBR is more flexible in process configuration, easier for modularized installation, and more convenient for automatic operation. These provide MBR with additional opportunities for applications in the areas of, for example, specific industrial wastewater treatment, decentralized wastewater treatment (such as in rural areas), and anaerobic processes (such as AnMBR).

## Slide 17: Hygiene water quality
  Faecal coliform is usually employed as an indicator of pathogenic bacteria in wastewater reclamation and reuse standards
Biological Wastewater Treatment
Online Course Series
Notes: Let’s continue to look into the hygiene water quality of the MBR effluent. ######## The presence of pathogens is of primary concern in wastewater reclamation and reuse for the purposes of, for example, ######## lavatory flushing, vehicle washing, urban greening, recreational environment reuse, and farmland irrigation. Pathogens that affect hygiene water quality cover a wide range of protozoa /ˌprəutəu'zəuə/, helminths (as well as their eggs), fungal spores, pathogenic bacteria (such as faecal coliform and enterococci), and viruses (such as enterovirus, adenovirus /ə,dino'vaɪrəs/, and norovirus). The health risks due to direct or indirect human exposure to these pathogens should be seriously considered when designing wastewater reclamation processes. ######## Faecal coliform is usually employed as an indicator of pathogenic bacteria in wastewater reclamation and reuse standards. It is noted that pathogenic bacteria are also subject to wastewater discharge standards, due to their profound risks to the ecosystems and public health.

## Slide 18: Hygiene water quality
Biological Wastewater Treatment
Online Course Series
  F-specific coliphage, somatic coliphage, and phage T4 are often employed as indicators of viruses in MBR research
Notes: F-specific coliphage /ˈkoləˌfedʒ/, somatic coliphage, and phage T4 are often employed as indicators of viruses in MBR research.

## Slide 19: Hygiene water quality
Comparison between membrane pore size and pathogens
  Directly rejecting pathogens larger than the pores
Membrane
Bacteria
Colloids
Solutes
Sludge flocs
Biological Wastewater Treatment
Online Course Series
Notes: The left Figure shows a comparison between the sizes of membrane pores and different pathogens. It is clear that the microfiltration or ultrafiltration membranes can effectively reject protozoa, helminths, fungal spores, and bacteria, because they are larger than the membrane pores.

## Slide 20: Hygiene water quality
  The logarithmic removal (LRV) of E. coli and enterococci by MBR was approximately 3 orders higher than that by CAS.
Removal mechanisms of Pathogens
  Directly rejecting pathogens larger than the pores
Membrane
Bacteria
Colloids
Solutes
Sludge flocs
Removal efficiencies of bacteria and viruses in
full‐scale MBR and CAS plants
Biological Wastewater Treatment
Online Course Series
Notes: This figure shows a comparison of the removal efficiencies of bacteria and viruses between the full‐scale MBR and Conventional Activated Sludge plants. As shown in this Figure, ######## a survey of full-scale Wastewater treatment plants (WWTPs) shows that the logarithmic removal of E. coli and enterococci by MBR was approximately 3 orders higher than that by Conventional Activated Sludge. ######## However, unlike the obvious rejection of bacteria by the membrane via steric exclusion, the rejection of viruses is not certain, because the sizes of the viruses are comparable or even smaller than the membrane pores.

## Slide 21: Hygiene water quality
Removal efficiencies of bacteria and viruses in
full‐scale MBR and CAS plants
Removal mechanisms of Pathogens
  Removal rate of the tested viruses by MBR was much higher than that by CAS plants
  Removal mechanisms for virus
  Partial rejection by the membranes
  Rejection by the gel layer
  Attachment to larger particle size pollutants
  Microbial inactivation in the mixed sludge
Biological Wastewater Treatment
Online Course Series
Notes: As shown in the right figure, the full-scale MBRs achieve a 3-6 log removal of the tested viruses, which are much higher than the Conventional Activated Sludge plants do. The Conventional Activated Sludge plants only achieve a 1-3 log removal.
######## The removal mechanisms of viruses are complicated and have not yet been fully understood. There are several explanations in the literature. A prevailing one is that the membrane and the gel/cake foulant layer together act as a composite filter in tandem to achieve increased rejection of viruses.
Firstly, the membrane itself can partly reject viruses, with the rejection rate depending on the pore size. Secondly, the pore channels can be narrowed due to adsorption of foulants onto the pore walls. The gel layer is a matrix of biopolymers with high porosity and water content but very low permeability, and it is compressible and becomes denser at higher transmembrane pressures. The effective pore size of the calcium alginate gel layer is estimated to be 5-30 nm. The gel layer can contribute largely to the overall rejection of viruses. It should be noted, however, that overgrowth of the gel layer exacerbates membrane fouling.
In addition, the viruses can attach to the suspended solids in the mixed liquor, or be entrapped into the sludge flocs, and be rejected by the membrane. Microbial inactivation of the viruses in the sludge mixed liquor is also a possible mechanism for the removal.

## Slide 22: Hygiene water quality
  Compared with chemical disinfection technologies (such as chlorination, UV radiation, and advanced oxidation), membrane-based rejection of the pathogens is a gentle physical process that bypasses the risks of disinfection by-products, germ resistance, and involuntary mutations.
Biological Wastewater Treatment
Online Course Series
Notes: And compared with chemical disinfection technologies (such as chlorination, UV radiation, and advanced oxidation), membrane-based rejection of the pathogens is a gentle physical process that bypasses the risks of disinfection by-products, germ resistance, and involuntary mutations.

## Slide 23: Emerging pollutant removal
Image Source: Syed Saquib et al., Chapter 19 - Emerging pollutants in water and human health, in Contamination of Water (Academic Press, 2021).
Emerging pollutant
Feature
Exerting acute or chronic toxicity at trace concentrations
Usually persistent or pseudo-persistent in the aquatic environment
Biological Wastewater Treatment
Online Course Series
Notes: Emerging pollutant or trace organic pollutants have raised public concerns for water safety. ######## These pollutants can exert acute or chronic toxicity even at trace concentrations, and are usually persistent or pseudo-persistent in the aquatic environment. So, the occurrence of emerging pollutant in the effluents of Wastewater treatment plants (WWTPs) should be seriously considered, no matter whether the effluents are to be discharged or reused.

## Slide 24: Emerging pollutant removal
TrOPs: trace organic pollutants; EDC: Endocrine disrupting compounds; PPCPs: Pharmaceutical and personal care products.
Trace Organic Pollutants (TrOPs)
Note: The pollutants listed here are just the tip of the iceberg. There are far more TrOPs, including synthetic chemicals and intermediate metabolites, yet to be properly monitored and unveiled.
phenolic
compounds
steroidal
estrogens
EDCs
alkylphenols
alkylphenol
polyethoxylates
……
……
1 ng/L-1 µg/L
antibiotics
sulfonamides
quinolones
macrolides
……
analgesic
drugs
……
analgesic
drugs
anti-
inflammatory
PPCPs
10 ng/L-10 µg/L
Personal care products
Biological Wastewater Treatment
Online Course Series
Notes: The most widely investigated trace organic pollutants (TrOPs) include endocrine /'ɛndəkrɪn/ disrupting compounds (EDCs) and pharmaceutical and personal care products (PPCPs). They are categorized according to the impacts and usage.
EDCs include a range of phenolic compounds and steroidal estrogens. PPCPs can be classified, according to their medical effects, into: anti-inflammatory and analgesic /'ænl'dʒizɪk/ drugs, antibiotics, lipid regulating drugs, musks, among others. The individual concentrations of the known EDCs in the municipal wastewater typically range from 1 ng/L to 1 µg/L. The individual concentrations of detectable PPCPs are usually 10 ng/L to 10 µg/L. ######## It is noteworthy that the pollutants listed here are just the tip of the iceberg. There are far more TrOPs, yet to be properly monitored and unveiled.

## Slide 25: Emerging pollutant removal
  Widely varied biodegradability and
  hydrophobicity of the compounds
  Chemical structure of the compounds
    Half of the TrOPs exhibited a high removal rate of over 95%
    Two thirds of the TrOPs had a removal rate of over 80%
    A few PPCPs had a removal efficiency lower than 20%
  The removal efficiencies of EDCs and PPCPs in full-scale MBRs
Biological Wastewater Treatment
Online Course Series
Notes: The removal efficiencies of EDCs and PPCPs in full-scale MBRs is shown in the figure. ######## About half of the TrOPs exhibited a high removal rate of over 95%, and two thirds of the TrOPs had a removal rate of over 80%, whereas a few PPCPs had a removal efficiency lower than 20%. ######## The large variability in the removal performance was attributable to the widely varied biodegradability and hydrophobicity. ######## Both of them stem from the chemical structure of the compounds.

## Slide 26: Emerging pollutant removal
The process emerging pollutants undergo in the MBR
01
02
03
04
  Adsorption
  Degradation
  Rejection
  Evaporation
Biological Wastewater Treatment
Online Course Series
Notes: So, what might happen when the emerging pollutants enter an MBR system? the emerging pollutants in the MBR system may undergo adsorption, degradation, rejection, and evaporation.

## Slide 27: Emerging pollutant removal
    Adsorbed by the bacterial cells, EPS, suspended solids, and colloids
    Mainly determined by the hydrophobicity of TrOPs
The process emerging pollutants undergo in the MBR
01
02
03
04
  Adsorption
  Degradation
  Rejection
  Evaporation
Biological Wastewater Treatment
Online Course Series
Notes: The first is absorption, ######## pollutants can be adsorbed by the bacterial cells, EPS, suspended solids, and colloids in the mixed liquor. The adsorption is mainly determined by the hydrophobicity of the pollutants, which is reflected by the octanol/water partition coefficient (Kow). After being adsorbed into the sludge phase, the pollutants may then undergo biodegradation, and the two-step process can be described by a two-phase fate model where the sludge-water partition coefficient, water-sludge mass transfer rate constant, and biodegradation rate constant are the key parameters.
In addition, the adsorption may be strengthened by adding adsorbents such as powdered activated carbon (PAC) into the MBR system. The membrane will guarantee complete rejection of the adsorbent particles. Note that adsorption is merely a physical process that transfers the TrOPs from the aqueous phase to the solid/sludge phase. Ultimate removal of the pollutants still relies on degradation or proper disposal of the excess sludge. For TrOPs that are neither adsorbable nor biodegradable, advanced treatment (such as ozonation and nanofiltration) is incorporated into the system to ensure high quality of the effluent. TrOPs may undergo biodegradation after being absorbed.

## Slide 28: Emerging pollutant removal
    Adsorbed by the bacterial cells, EPS, suspended solids, and colloids
    Mainly determined by the hydrophobicity of TrOPs
    Be strengthened by adding adsorbents (e.g. powdered activated carbon)
The process emerging pollutants undergo in the MBR
01
02
03
04
  Adsorption
  Degradation
  Rejection
  Evaporation
Biological Wastewater Treatment
Online Course Series
Notes: The first is absorption, ######## pollutants can be adsorbed by the bacterial cells, EPS, suspended solids, and colloids in the mixed liquor. The adsorption is mainly determined by the hydrophobicity of the pollutants, which is reflected by the octanol/water partition coefficient (Kow). After being adsorbed into the sludge phase, the pollutants may then undergo biodegradation, and the two-step process can be described by a two-phase fate model where the sludge-water partition coefficient, water-sludge mass transfer rate constant, and biodegradation rate constant are the key parameters.
In addition, the adsorption may be strengthened by adding adsorbents such as powdered activated carbon (PAC) into the MBR system. The membrane will guarantee complete rejection of the adsorbent particles. Note that adsorption is merely a physical process that transfers the TrOPs from the aqueous phase to the solid/sludge phase. Ultimate removal of the pollutants still relies on degradation or proper disposal of the excess sludge. For TrOPs that are neither adsorbable nor biodegradable, advanced treatment (such as ozonation and nanofiltration) is incorporated into the system to ensure high quality of the effluent. TrOPs may undergo biodegradation after being absorbed.

## Slide 29: Emerging pollutant removal
The process emerging pollutants undergo in the MBR
01
02
03
    The removal efficiencies by MBR and CAS are comparable for readily degradable TrOPs.
    Be more effective in biological degradation than CAS for refractory TrOPs
    Be mainly dependent on their biodegradability and hydrophobicity
04
  Adsorption
  Degradation
  Rejection
  Evaporation
TrOPs
Membrane tank
Bacteria
Biological Wastewater Treatment
Online Course Series
Notes: The second is degradation. ######## For TrOPs which are readily degradable, the removal efficiencies by MBR and Conventional Activated Sludge are normally comparable, whereas for refractory TrOPs, the MBR is more effective in biological degradation. This can be attributed to the adsorption of TrOPs by sludge and EPS and the membrane interception of MBR. For TrOPs with strong hydrophobicity that are readily adsorbable by the sludge, the higher sludge concentrations as well as probably higher EPS contents in the MBR are conducive to the TrOPs uptake, but the longer Sludge Retention Time (SRT) is unfavourable for the discharge of excess sludge. For TrOPs with weaker hydrophobicity but still adsorbable by the particles and colloids in the mixed liquor, the MBR is advantageous in rejecting these chemicals and improving the effluent quality. Overall, the removal efficiencies are jointly influenced by the mixed liquor properties (e.g. MLSS and EPS) and the operational conditions (such as Sludge Retention Time (SRT)). In short, the removal efficiencies of TrOPs are mainly dependent on their biodegradability and hydrophobicity.

## Slide 30: Emerging pollutant removal
The process emerging pollutants undergo in the MBR
01
02
03
04
  Adsorption
  Degradation
  Rejection
  Evaporation
    Direct retention by MF or UF membrane is marginal
    Adsorption and size exclusion by the gel/cake layer
Biological Wastewater Treatment
Online Course Series
Notes: The third is rejection, ######## The microfiltration or ultrafiltration membrane has a marginal effect on the direct retention of TrOPs. Some initial removal may be observed, but this is probably due to initial short-term physical adsorption into the pores. However, the adsorption and size exclusion by the gel/cake layer are non-negligible. The TrOPs can be readily rejected when they are adsorbed in the sludge phase or bound to colloids. Due to the efficiency of membrane rejection, MBR is superior to Conventional Activated Sludge in removing most ARBs and ARGs. Besides, the MBR can achieve over 99% removal of microplastics, owing to the evident superiority of membrane rejection.

## Slide 31: Emerging pollutant removal
The process emerging pollutants undergo in the MBR
01
02
03
04
  Adsorption
  Degradation
  Rejection
  Evaporation
    Evaporated under the aeration conditions in the aerobic or membrane tanks
    Particularly for TrOPs with large values for Henry’s constant
Membrane tank
TrOPs
Biological Wastewater Treatment
Online Course Series
Notes: Lastly, a small portion of TrOPs may evaporate under the aeration conditions in the aerobic or membrane tanks.

## Slide 32: Emerging pollutant removal
  Biological responses to the pharmaceuticals in wastewater systems
Antibiotic resistance genes
(ARGs)
  MBR outperforms CAS in the removal of most ARB and ARGs, owing to the efficiency of membrane rejection.
  Some ARGs still persist in the membrane effluent, further efforts are required to achieve a thorough elimination of these substances.
WWTPs
Antibiotic resistant bacteria
(ARB)
Antibiotic residues
Biological Wastewater Treatment
Online Course Series
Notes: The biological responses to the pharmaceuticals in wastewater systems are also noteworthy. ######## Wastewater treatment plants (WWTPs) are potential reservoirs of antibiotic residues, antibiotic resistant bacteria (ARB), and antibiotic resistance genes (ARGs), and the release of these contaminants into the environment is considered to be risky to the ecosystems and human health. ######## It has been reported that the MBR outperforms Conventional Activated Sludge in the removal of most ARB and ARGs, owing to the efficiency of membrane rejection. However, some ARGs still persist in the membrane effluent, and further efforts are required to achieve a thorough elimination of these substances.

## Slide 33: Emerging pollutant removal
  Microplastics in wastewater systems
Difficult to settle in sedimentation tanks
Having not been satisfactorily removed in conventional WWTPs
MBR can achieve over 99% removal of microplastics, owing to the evident superiority of membrane rejection.
Potential ecotoxicological impacts
Persistence in the environment
Microplastics, commonly defined as plastic particles smaller than 5 mm.
Microplastics
Biological Wastewater Treatment
Online Course Series
Notes: Microplastics, commonly defined as plastic particles smaller than 5 mm, have recently raised public concerns for human health and ecological safety due to their potential ecotoxicological impacts and persistence in the environment. ######## These materials are difficult to settle in sedimentation tanks and, as such, have not been satisfactorily removed in conventional Wastewater treatment plants (WWTPs). ######## In comparison, the MBR can achieve over 99% removal of microplastics, owing to the evident superiority of membrane rejection. The membrane can serve as an effective barrier to block the discharge of microplastics from Wastewater treatment plants (WWTPs) into the environment.

## Slide 34: Energy recovery
A stream that contains valuable resources
  Anaerobic
  treatment
Biological Wastewater Treatment
Online Course Series
Notes: Nowadays, wastewater is regarded as a stream that contains valuable resources rather than just a contaminant. and energy and resource recovery from wastewater is a vital development aspect of a sustainable wastewater treatment system besides water purification. ######## The anaerobic treatment process is technically promising to realize this goal, and AnMBRs are attracting lots of attention due to their advantages in retention of slow-growing anaerobes, excellent and stable effluent quality, efficient bioenergy production, their small footprint, etc.
######## Anaerobic treatment technology is expected to achieve energy recovery. AnMBRs enables methane energy recovery while water purification. To date, AnMBRs have been successfully applied to treat high-strength wastewater with COD of 102-103 mg/L, with pollutant removal efficiencies of mostly >90%. With relatively low organic strength but large water volume, municipal wastewater treatment has recently become a hot application field of AnMBRs, and various configurations and modifications have been proposed to enhance the treatment performance and methane production. In general, AnMBRs produce 0.1-0.5 m3CH4/kgCODremoved of methane in municipal wastewater treatment.

## Slide 35: Energy recovery
A stream that contains valuable resources
  Anaerobic
  treatment
CH4
Energy (i.e. Methane)
  Anaerobic Membrane Bioreactors (AnMBRs)
    Water purification
      High-strength wastewater with COD of 102-103 mg/L
      Pollutant removal efficiencies >90%.
    Energy and resource recovery
      0.1-0.5 m3 CH4/kgCODremoved of methane in municipal wastewater treatment were produced
Biological Wastewater Treatment
Online Course Series
Notes: Nowadays, wastewater is regarded as a stream that contains valuable resources rather than just a contaminant. and energy and resource recovery from wastewater is a vital development aspect of a sustainable wastewater treatment system besides water purification. ######## The anaerobic treatment process is technically promising to realize this goal, and AnMBRs are attracting lots of attention due to their advantages in retention of slow-growing anaerobes, excellent and stable effluent quality, efficient bioenergy production, their small footprint, etc.
######## Anaerobic treatment technology is expected to achieve energy recovery. AnMBRs enables methane energy recovery while water purification. To date, AnMBRs have been successfully applied to treat high-strength wastewater with COD of 102-103 mg/L, with pollutant removal efficiencies of mostly >90%. With relatively low organic strength but large water volume, municipal wastewater treatment has recently become a hot application field of AnMBRs, and various configurations and modifications have been proposed to enhance the treatment performance and methane production. In general, AnMBRs produce 0.1-0.5 m3CH4/kgCODremoved of methane in municipal wastewater treatment.

## Slide 36: Energy recovery
  Influencing factors of methane production
  Bacterial competition
  Operational parameters
    pH
    Fermentation temperature
    Organic loading rate
Biological Wastewater Treatment
Online Course Series
    Mesophilic (20-42°C)
    Psychrophilic (0-20°C)
    Neutral
    6 kgCOD/m3.d
    0.382 m3CH4/kgCODremoved
Notes: Methane production in AnMBRs is affected by both operational parameters and the bacterial competition in the reactors. ######## As for the operational parameters, the fermentation temperature, pH, and organic loading rate can significantly influence the methane production. ######## For the fermentation temperature, the mesophilic (20-42°C) and psychrophilic (0-20°C) conditions are favoured for AnMBRs, and higher methane yield was observed at higher temperatures. ######## Besides, the neutral pH condition and an appropriate organic loading rate are also crucial parameters of biogas yield, ######## and a theoretical optimal methane production of 0.382 m3CH4/kgCODremoved was proposed at an organic loading rate of 6 kgCOD/m3.d for AnMBRs treating municipal wastewater.
######## As for the bacterial competition, it can also affect methane production. For example, if the organic load is insufficient and the sulfate content is high, the methane production will be affected due to the internal competition between sulphate-reducing bacteria and methane-poroducing archaea for organic substances.

## Slide 37: Energy recovery
  Influencing factors of methane production
  Bacterial competition
    Insufficient organic load
    High sulphate content
    Internal competitions between sulphate-reducing bacteria and methane-producing archaea
  Operational parameters
    pH
    Fermentation temperature
    Organic loading rate
Biological Wastewater Treatment
Online Course Series
    Mesophilic (20-42°C)
    Psychrophilic (0-20°C)
    Neutral
    6 kgCOD/m3.d
    0.382 m3CH4/kgCODremoved
Notes: Methane production in AnMBRs is affected by both operational parameters and the bacterial competition in the reactors. ######## As for the operational parameters, the fermentation temperature, pH, and organic loading rate can significantly influence the methane production. ######## For the fermentation temperature, the mesophilic (20-42°C) and psychrophilic (0-20°C) conditions are favoured for AnMBRs, and higher methane yield was observed at higher temperatures. ######## Besides, the neutral pH condition and an appropriate organic loading rate are also crucial parameters of biogas yield, ######## and a theoretical optimal methane production of 0.382 m3CH4/kgCODremoved was proposed at an organic loading rate of 6 kgCOD/m3.d for AnMBRs treating municipal wastewater.
######## As for the bacterial competition, it can also affect methane production. For example, if the organic load is insufficient and the sulfate content is high, the methane production will be affected due to the internal competition between sulphate-reducing bacteria and methane-poroducing archaea for organic substances.

## Slide 38: Energy recovery
  Existing problems in AnMBRs
    Methane loss
Biological Wastewater Treatment
Online Course Series
    Membrane fouling
    Methane
    Dissolved
    Effluent
    Temperature-related
    Higher solubility of methane at lower temperature causes more methane loss
Notes: Currently, the AnMBR technology is still facing some challenges, including methane loss and membrane fouling. ######## The methane loss mainly indicates the dissolved methane in the effluent. This phenomenon is temperature-related. Higher solubility of methane at lower temperature causes more methane loss especially in hydraulic pressure-driven AnMBRs. Correspondingly, harvesting the dissolved methane in permeate is worth investigating from perspectives of both increasing biogas efficiency and reducing greenhouse gas emission.
######## Besides, membrane fouling in AnMBRs is also unavoidable. To achieve a steady operation of AnMBRs, multiple fouling control strategies can be applied including optimizing operational conditions, dosing additives (such as granular activated carbon), increasing the shear force on the membrane surface by mechanical movement or biogas sparging, regulating chemical cleaning, etc. It should be noted that, with further research and development, AnMBR has a promising practical application to achieve efficient energy recovery from municipal wastewater treatment.

## Slide 39: Energy recovery
  Existing problems in AnMBRs
    Methane loss
Biological Wastewater Treatment
Online Course Series
    Membrane fouling
    Methane
    Dissolved
    Effluent
    Temperature-related
    Higher solubility of methane at lower temperature causes more methane loss
  Fouling control strategies
      Optimizing operational conditions
      Dosing additives (e.g., granular activated carbon)
      Increasing shear force on membrane surface
      regulating chemical cleaning
      ……
Notes: Currently, the AnMBR technology is still facing some challenges, including methane loss and membrane fouling. ######## The methane loss mainly indicates the dissolved methane in the effluent. This phenomenon is temperature-related. Higher solubility of methane at lower temperature causes more methane loss especially in hydraulic pressure-driven AnMBRs. Correspondingly, harvesting the dissolved methane in permeate is worth investigating from perspectives of both increasing biogas efficiency and reducing greenhouse gas emission.
######## Besides, membrane fouling in AnMBRs is also unavoidable. To achieve a steady operation of AnMBRs, multiple fouling control strategies can be applied including optimizing operational conditions, dosing additives (such as granular activated carbon), increasing the shear force on the membrane surface by mechanical movement or biogas sparging, regulating chemical cleaning, etc. It should be noted that, with further research and development, AnMBR has a promising practical application to achieve efficient energy recovery from municipal wastewater treatment.

## Slide 40: Summary
  Ordinary pollutant removal
  Hygiene water quality
  Emerging pollutant removal
  Energy recovery
Biological Wastewater Treatment
Online Course Series
Notes: As a summary, in this section, we learned about the removal performance of MBRs for ordinary pollutants and emerging pollutants. We also learned about the hygiene water qualities of the MBR effluent. At last, we learned about the development potential of MBRs in energy recovery. ######## I hope you enjoyed this section. Thank you!