## Slide 1
Course on Membrane Bioreactors
Membrane Fouling
Characterization
Fangang Meng
Yu-Xi Huang

## Slide 2: Contents
  Definition of membrane fouling
  Characterization methods
Biological Wastewater Treatment
Online Course Series

## Slide 3: Definition of membrane fouling
Source: Meng, et al., Water Research, 2008; 43(6), 1489-1512.
Membrane Fouling
The accumulation of sludge flocs, colloids, solutes in membrane pores and/or membrane surfaces
EPS/SMP
microbe
cell debris
Inorganic ions
Time
Membrane
Cake layer
TMP
Reduction of permeate flux
Increase of transmembrane pressure (TMP)
Biological Wastewater Treatment
Online Course Series

## Slide 4: Definition of membrane fouling
Reversible Fouling
Reversible fouling can be easily eliminated by implementation of physical cleaning
Bio-cake disruption
Physical cleaning
  Easily eliminated
  Loosely attached foulants
  Formation of cake layer
Membrane pores
Biological Wastewater Treatment
Online Course Series

## Slide 5: Definition of membrane fouling
Irreversible Fouling and Irrecoverable Fouling
Irreversible fouling that can be readily removed by chemical cleaning
Irrecoverable fouling which cannot be removed by any approaches
  Needs chemical cleaning
  Pore blocking and strongly attached foulants
In comparison, the accumulation of irrecoverable fouling can be considered as a potential indicator of the deterioration of membrane
performance
Biological Wastewater Treatment
Online Course Series

## Slide 6: Characterization methods
Source: Zhang, et al., Biotechnology for Biofuels, 2021, 14(1): 158.
Polysaccharides are composed of numerous blocks,
such as α-guluronic acid (i.e., GG) and β-mannuronic acid (i.e., MM)
Biological Wastewater Treatment
Online Course Series
Compound Level — Polysaccharides

## Slide 7: Characterization methods
Compound Level — Polysaccharides
The large size of polysaccharides, leading to the higher accumulation potentials of polysaccharides in both mixed liquor and bio-cake
Polysaccharides have a strong gelling propensity, which is associated with the cross-linked structure of polysaccharide molecules
The presence of multi-valent cations in wastewater streams can considerably increase the gel layer formation on membranes
Fouling characteristics of polysaccharides
Biological Wastewater Treatment
Online Course Series

## Slide 8: Characterization methods
Source: Zhu, et al., ACS EST Water 2022, 2, 12, 2716–2723
Compound Level — Proteins and Humic Substances
Humic substances are expected to incorporate with other types of compounds, such as polysaccharides and proteins, via hydrophobic and electrostatic interactions
Proteins and polysaccharides were also found to participate in non-covalent interaction
Involvement of proteins and humic substances – making MBR fouling more complex
Biological Wastewater Treatment
Online Course Series
Notes: 标题中的proteins and humic substances, 首字母是不是需要大写？

## Slide 9: Characterization methods
Biofilm formation is normally started by the initial attachment of bacteria or microorganisms to membranes
The deposited bacteria or the developed biofilms on membranes can produce a large amount of EPS or SMP and may contribute to the biopolymer accumulation on membranes
Compound Level-Biofilm
Biological Wastewater Treatment
Online Course Series
Notes: SMP，标题中的biofilm首字母，大写？

## Slide 10: Characterization methods
Source: Ni, et al., Trends in biotechnology, 2011, 29(9): 454-463.
SMP are soluble organic compounds that are released during normal biomass metabolism and decay in mixed culture biotechnology
SMP compounds play an important role in the initial fouling stage
Based on bioassay tests and multi-exponential G models, biopolymers in the bio-cake were found to be dominated by slowly biodegradable polysaccharides that originated from SMP
Soluble microbial products (SMP)
Biological Wastewater Treatment
Online Course Series

## Slide 11: Characterization methods
Extracellular Polymeric Substances (EPS)
Bacteria deposition as well as biofilm development
on membranes is another key factor leading to
membrane fouling development
Biological Wastewater Treatment
Online Course Series
Notes: SMP

## Slide 12: Characterization methods
EPS is a complex mixture of high-molecular-weight polymers and can be categorized into two types based on solubility
  bound EPS (bEPS)
  Soluble EPS (sEPS): similar to soluble microbial products (SMP)
EPS produced by the deposited microbial cells becomes a major foulant after the TMP jump
The presence of high concentrations of EPS in sludge significantly undermines its ability to form flocs, resulting in poor sedimentation performance
Biological Wastewater Treatment
Online Course Series
Extracellular Polymeric Substances (EPS)
Notes: SMP

## Slide 13: Characterization methods
Species Level
High throughput sequencing
Molecular
biology
Unclear ecological mechanism of membrane fouling
Determinative
Randomness
Microbial diversity and structure
The ecological process driving membrane fouling?
Interactions between species?
Clarifying the assembly mechanism of microorganisms is crucial for
deepening our understanding and providing a theoretical basis for
optimizing fouling control methods
Biological Wastewater Treatment
Online Course Series

## Slide 14: Characterization methods
In the Future
Understanding of the dynamic changes in both biopolymers and bacteria in real MBR plants
A tracking method to identify the dynamic membrane fouling process and the foulant source
Understanding the functional and metabolic processes in bio-cake and multi-omics is recommended
Biological Wastewater Treatment
Online Course Series