## Slide 1
Course on Membrane Bioreactors
MBR plant design, O&M:
Process Composition and Pre-treatment
Kang Xiao
Notes: Hello everyone! I’m Jiao Zhang from Tsinghua University. In this Case study section, we are going to review several practical applications of MBR technology, which could help you better understand its usage and the effect in the whole treatment process.

## Slide 2: Contents
  Process composition
  Pretreatment
  Biological treatment units
  Membrane filtration system
Biological Wastewater Treatment
Online Course Series

## Slide 3: Process composition
  MBR-based wastewater treatment
Pretreatment
Biological
treatment
Membrane
filtration
Monitoring and control system
The design of the whole process should be compatible with the raw wastewater quality and treatment requirements, in terms of the removal of C/N/P and other pollutants.
Membrane modules/cassettes
Membrane tanks
Membrane filtration/aeration/ cleaning facilities
Biological Wastewater Treatment
Online Course Series

## Slide 4: Process composition
When COD and BOD are the main target and there is no requirement for TN or TP removal, a primitive aerobic MBR may be adequate for this purpose.
When the removal of TN is taken into account, an anoxic zone is required to compose the anoxic/aerobic-MBR (AO-MBR) process.
For simultaneous biological removal of N and P, the AAO-MBR process is needed.
Option 1: removal of C
Option 2: removal of C/TN
Option 3: removal of C/TN/TP
Biological Wastewater Treatment
Online Course Series

## Slide 5: Process composition
When COD and BOD are the main target and there is no requirement for TN or TP removal, a primitive aerobic MBR may be adequate for this purpose.
When the removal of TN is taken into account, an anoxic zone is required to compose the anoxic/aerobic-MBR (AO-MBR) process.
For simultaneous biological removal of N and P, the AAO-MBR process is needed.
Option 1: removal of C
Option 2: removal of C/TN
Option 3: removal of C/TN/TP
Biological Wastewater Treatment
Online Course Series

## Slide 6: Process composition
The AAO-MBR process is most commonly applied for municipal wastewater treatment.
Settled
sewage
Aerobic tank
Effluent
Air demand GO
Air demand GM
Recirculation R1
Recirculation R2
Recirculation R3
Excess sludge
Anaerobic tank
A1
Anoxic tank
A2
O
Membrane tank
M
Biological Wastewater Treatment
Online Course Series

## Slide 7: Process composition
The AAO-MBR process is most commonly applied for municipal wastewater treatment.
Settled
sewage
Aerobic tank
Effluent
Air demand GO
Air demand GM
Recirculation R1
Recirculation R2
Recirculation R3
Excess sludge
Anaerobic tank
A1
Anoxic tank
A2
O
Membrane tank
M
Biological Wastewater Treatment
Online Course Series

## Slide 8: Process composition
Several customized variants of the AAO-MBR process have been developed
through modifying the spatial locations of the A/O tanks, the temporal alternation of the A/O tanks, the routes of raw wastewater, and the routes of mixed liquor recirculation.
Recirculation R3
Membrane tank
Anaerobic tank
Aerobic tank
Anoxic tank
Anoxic tank
Air demand GO
Air demand GM
External carbon
Settled
sewage
Effluent
Recirculation R1
Recirculation R2
Excess sludge
Example: AAOA-MBR process
Scenario: insufficient carbon source (low C/N ratio)
Additional
A1
A2
A2
O
M
Biological Wastewater Treatment
Online Course Series

## Slide 9: Process composition
Several customized variants of the AAO-MBR process have been developed through modifying the spatial locations of the A/O tanks, the temporal alternation of the A/O tanks, the routes of raw wastewater, and the routes of mixed liquor recirculation.
Example: two-stage AO-MBR process
Scenario: for thorough utilization of endogenous carbon source
Air demand GO1
Air demand GM
External carbon
Recirculation R1
Recirculation R2
Excess
sludge
Membrane tank
Anaerobic tank
Aerobic tank
Anoxic tank
Anoxic tank
Aerobic tank
Effluent
Air demand GO2
Side-stream
Settled
sewage
Recirculation R3
2nd stage
A1
A2
O
M
A2
O
Biological Wastewater Treatment
Online Course Series

## Slide 10: Process composition
Several customized variants of the AAO-MBR process have been developed through modifying the spatial locations of the A/O tanks, the temporal alternation of the A/O tanks, the routes of raw wastewater, and the routes of mixed liquor recirculation.
Example: side-stream of wastewater
Scenario: to save the carbon source for denitrification
Air demand GO1
Air demand GM
External carbon
Recirculation R1
Recirculation R2
Excess
sludge
Membrane tank
Anaerobic tank
Aerobic tank
Anoxic tank
Anoxic tank
Aerobic tank
Effluent
Air demand GO2
Settled
sewage
Recirculation R3
Side-stream
A1
A2
O
M
A2
O
Biological Wastewater Treatment
Online Course Series

## Slide 11: Process composition
Source: Xiao et al. Engineering application of membrane bioreactor for wastewater treatment in China: Current state and future prospect. Frontiers of Environmental Science and Engineering, 2014(8): 805-819.
Several customized variants of the AAO-MBR process have been developed through modifying the spatial locations of the A/O tanks, the temporal alternation of the A/O tanks, the routes of raw wastewater, and the routes of mixed liquor recirculation.
Process flow | Process feature
 | Bypassing reverse AAO-MBR, to save carbon source for denitrification and diminish adverse impact of aerobic recirculation on the anaerobic zone
 | University of Cape Town (UCT)-MBR, a variant of AAO-MBR, to diminish adverse impact of aerobic recirculation on the anaerobic zone
 | Bypassing UCT-MBR, to save carbon source for denitrification
 | Modified UCT-MBR, one more anoxic zone than UCT-MBR, to enhance endogenous denitrification
 | Similar to multi-stage AO-MBR, a second anoxic zone after the aerobic zone to enhance endogenous denitrification
 | An additional zone (X) after the aerobic zone, switchable between anoxic and aerobic, to increase the flexibility of process adjustment
Biological Wastewater Treatment
Online Course Series

## Slide 12: Process composition
Industrial
Wastewater
Printing and dyeing wastewater
large water volume, high content of organic pollutants, and high alkalinity
Medical wastewater
pathogens, refractory organic compounds, and/or radioactive pollutants
Food industry wastewater
high suspended solids and oil content, large BOD5/COD value, and high nitrogen and phosphorus content
Chemical wastewater
highly toxic and refractory pollutants, with varied acidity or alkalinity
Electronic wastewater
containing various heavy metal ions, cyanide, acidic and alkaline substances, highly toxic and refractory
Mining wastewater
high turbidity, poor settleability of SS, high COD, and toxic and harmful heavy metal ions
Biological Wastewater Treatment
Online Course Series

## Slide 13: Process composition
Pretreatment (prior to MBR-based biological treatment)
Oil/water separation
Floatation
Coagulation and chemical precipitation
pH conditioning
Hydrolysis-acidification
Post-treatment (after MBR-based biological treatment)
Activated carbon adsorption
Advanced oxidation
Biological aerated filter treatment
Further membrane separation (NF, RO, etc.)
Special considerations for industrial wastewater treatment:
Specific configuration of the whole process depends on the wastewater quality and the treatment goal
Biological Wastewater Treatment
Online Course Series

## Slide 14: Process composition
Some examples of industrial wastewater treatment process from the literature:
Wastewater source | Treatment process
Industrial park | → regulating → acidification → A2/A1/A2/O-M → disinfection
Industrial park (coal chemical) | → air floatation precipitation → acidification → A2/A1/O/A2/O/A2/O-M → disinfection
Industrial park (dyeing) | → regulating → pH neutralization → acidification → O-M → advanced oxidation (O3)
Industrial park (food) | → regulating → acidification → A1/A2/O-M → disinfection
Iron & steel | → regulating → pH regulating → air floatation → EGSB → A2/O-M
Fine chemical (pharmaceutical) | → sedimentation→ pre-Acidification → IC anaerobic → A2/O-M →BAF
Petro-chemical | → regulating → deoiling → air floatation → acidification → O/O-M → sedimentation → BAF
Coal chemical | → secondary effluent → A1/O-M
Coal chemical | → regulating → EC anaerobic → A1/O → sedimentation → M → advanced oxidation (O3)
Electronic & electroplating | → pH regulating → A1/A2/O-M → disinfection → RO
BAF: biological aerated filter
EC: external circulation anaerobic reactor
IC: internal circulation anaerobic reactor
EGSB: anaerobic expanded granular sludge bed
RO: reverse osmosis
Source: Zhang et al. Large-scale membrane bioreactors for industrial wastewater treatment in China: Technical and economic features, driving forces, and perspectives. Engineering, 2021 (7): 868-880.
M: membrane unit
A1: anaerobic zone
A2: anoxic zone
O: aerobic zone
Biological Wastewater Treatment
Online Course Series

## Slide 15: Process composition
Some examples of industrial wastewater treatment process from the literature:
Wastewater source | Treatment process
Industrial park | → regulating → acidification → A2/A1/A2/O-M → disinfection
Industrial park (coal chemical) | → air floatation precipitation → acidification → A2/A1/O/A2/O/A2/O-M → disinfection
Industrial park (dyeing) | → regulating → pH neutralization → acidification → O-M → advanced oxidation (O3)
Industrial park (food) | → regulating → acidification → A1/A2/O-M → disinfection
Iron & steel | → regulating → pH regulating → air floatation → EGSB → A2/O-M
Fine chemical (pharmaceutical) | → sedimentation→ pre-Acidification → IC anaerobic → A2/O-M →BAF
Petro-chemical | → regulating → deoiling → air floatation → acidification → O/O-M → sedimentation → BAF
Coal chemical | → secondary effluent → A1/O-M
Coal chemical | → regulating → EC anaerobic → A1/O → sedimentation → M → advanced oxidation (O3)
Electronic & electroplating | → pH regulating → A1/A2/O-M → disinfection → RO
BAF: biological aerated filter
EC: external circulation anaerobic reactor
IC: internal circulation anaerobic reactor
EGSB: anaerobic expanded granular sludge bed
RO: reverse osmosis
Source: Zhang et al. Large-scale membrane bioreactors for industrial wastewater treatment in China: Technical and economic features, driving forces, and perspectives. Engineering, 2021 (7): 868-880.
M: membrane unit
A1: anaerobic zone
A2: anoxic zone
O: aerobic zone
Biological Wastewater Treatment
Online Course Series

## Slide 16: Pretreatment
General pretreatment facilities
Influent
Pump Station
Grit Separation
Primary Sedimentation Tank
Bar screen or mesh screen
Coarse screen is used to remove larger floating and suspended substances, in order to protect the operation of pumps.
Fine screen is used to remove small suspended particles and reduce the operational load of subsequent sewage treatment.
Coarse Screen
16-25 mm
Fine Screen
1.5-10 mm
Ultrafine Screen
0.2-1 mm
Biological Wastewater Treatment
Online Course Series

## Slide 17: Pretreatment
General pretreatment facilities
Influent
Pump Station
Grit Separation
Primary Sedimentation Tank
Bar screen or mesh screen
Coarse screen is used to remove larger floating and suspended substances, in order to protect the operation of pumps.
Fine screen is used to remove small suspended particles and reduce the operational load of subsequent sewage treatment.
Ultrafine screen is used to remove small fibrous substances such as hair, in order to protect the membrane system.
Coarse Screen
16-25 mm
Fine Screen
1.5-10 mm
Ultrafine Screen
0.2-1 mm
Biological Wastewater Treatment
Online Course Series

## Slide 18: Pretreatment
Influent
Pump Station
Coarse Screen
Fine Screen
Grit Separation
Primary Sedimentation Tank
Ultrafine Screen
Grit separation
Grit chamber removes grit larger than 0.2 mm to avoid abrasion of the mechanical equipment and membrane modules and mitigate interference in the biological systems.
Aerated grit chamber recommended for MBR systems.
General pretreatment facilities
Biological Wastewater Treatment
Online Course Series
Oil and grease removal

## Slide 19: Pretreatment
Influent
Pump Station
Coarse Screen
Fine Screen
Grit Separation
Primary Sedimentation Tank
Ultrafine Screen
Primary sedimentation tank
Primary sedimentation tank is used to remove settleable suspended solids (SS) from wastewater.
HRT = 0.5-2 h (or 0.5-1 h when the wastewater has low C/N ratio).
hydraulic loading rate = = 1.5-4.5 m3/(m2·h)
flow rate (m3/h)
tank area (m2)
General pretreatment facilities
Biological Wastewater Treatment
Online Course Series
SS removal

## Slide 20: Pretreatment
Oil/water separation and floatation facilities
The pretreatment (and primary treatment) should ensure sufficient removal of oily substances.
Animal and vegetable oils: <50 mg/l
Petroleum-like substances: <5 mg/l
Other pretreatment facilities
Biological Wastewater Treatment
Online Course Series

## Slide 21: Pretreatment
Oil/water separation and floatation facilities
The pretreatment (and primary treatment) should ensure sufficient removal of oily substances
pH conditioning tank
When the pH of the wastewater is out of the range of 6-9 and becomes unsuitable for a biological system, a pH conditioning tank is required in the pretreatment section.
Other pretreatment facilities
Biological Wastewater Treatment
Online Course Series

## Slide 22: Pretreatment
[Aim] For industrial wastewater, the aim of pretreatment is to reduce the concentrations of SS, oily substances, and refractory pollutants, improve the biodegradability, and adjust the pH of the wastewater, which is critical to subsequent biological treatment.
[Special facilities] Wastewater pretreatment facilities may include oil separation, floatation, flocculation, pH conditioning, chemical precipitation, or hydrolysis-acidification units, according to the wastewater characteristics.
Oil/water separation and floatation
Petroleum industry
Chemical industry
Electronic industry
Papermaking and dyeing industry
Coagulation and chemical precipitation
pH conditioning
Hydrolysis-acidification and anaerobic sludge beds/blankets
and so on
Special considerations for pretreatment of industrial wastewater
……
Biological Wastewater Treatment
Online Course Series

## Slide 23: Pretreatment
Summary: The purpose of pretreatment is to:
remove impurities, reduce inorganic particles and SS, and reduce oil substances;
improve biodegradability, regulate pH condition, and facilitate reaction of biological units;
protect subsequent membrane filtration system.
Category | Facility | General function | Special consideration for MBR or wastewater characteristics
General pretreatment | Screen | Remove larger floating and suspended substances | Ultrafine screen to remove fibers to mitigate membrane clogging
 | Grit chamber | Remove grit to facilitate biological process and protect equipment | Protect membrane modules from abrasion
 | Primary sedimentation | Remove settleable SS | Adjust design parameter to save carbon source
Special pretreatment | pH conditioning | Adjust pH | Strong acidic or alkaline wastewater
 | Chemical precipitation | Remove impurities | Heavy metal wastewater
 | Coagulation | Aggregate SS and colloids | Highly toxic or refractory wastewater
 | Hydrolysis-acidification and anaerobic reactor | Improve biodegradability | High strength and/or low biodegradability
For MBR
Biological Wastewater Treatment
Online Course Series