## Slide 1
Course on Membrane Bioreactors
MBR plant design, O&M:
Biological Treatment Units
Kang Xiao

## Slide 2: Contents
  Process composition
  Pretreatment
  Biological treatment units
  Membrane filtration system
Biological Wastewater Treatment
Online Course Series

## Slide 3: Biological treatment units
Design of biological treatment units
Volume of the tanks
Mixed liquor recirculation routes and ratios
Excess sludge production
Aeration demand
Related to wastewater flow rate and quality, sludge concentration and loading rate, sludge yield and retention time, and/or reaction rate of the pollutants
Critical to affect distributions of DO concentrations, sludge concentrations, and pollutant removal efficiencies in the AAO-MBR tanks
To support oxidation reactions, DO concentration in separate O tank is recommended to be 1-2 mg/L
Important to the design of sludge discharge facilities; Should consider both biological sludge and chemical precipitates
An example of AAO-MBR
Biological Wastewater Treatment
Online Course Series

## Slide 4: Biological treatment units
Designing steps
1. Selection of process flow
2. Design of pretreatment/primary treatment
3. Design of biological treatment units
4. Design of membrane filtration system
4.1. Membrane flux and membrane area
4.2. Membrane aeration and cleaning
An example of AAO-MBR
A1
A2
O
M
Biological Wastewater Treatment
Online Course Series

## Slide 5: Biological treatment units
Designing steps
1. Selection of process flow
2. Design of pretreatment/primary treatment
3. Design of biological treatment units
3.1. Selection of design parameters
3.2. Tank volumes
3.2.1. Aerobic zone (O) 3.2.2. Anoxic zone (A2) 3.2.3. Anaerobic zone (A1)
3.3. Recirculation flow rates
3.4. Excess sludge production
3.5. Aeration demand for biological reactions
3.5.1. Oxygen demand 3.5.2. Air supply
4. Design of membrane filtration system
4.1. Membrane flux and membrane area
4.2. Membrane aeration and cleaning
An example of AAO-MBR
A1
A2
O
M
Biological Wastewater Treatment
Online Course Series

## Slide 6: Biological treatment units
Adopted from the ‘Technical Specification for Design of Membrane Bioreactor Processes for Municipal Wastewater Treatment’ (Chinese standard T/CECS152-2017).
Designing steps
1. Selection of process flow
2. Design of pretreatment/primary treatment
3. Design of biological treatment units
3.1. Selection of design parameters
3.2. Tank volumes
3.2.1. Aerobic zone (O) 3.2.2. Anoxic zone (A2) 3.2.3. Anaerobic zone (A1)
3.3. Recirculation flow rates
3.4. Excess sludge production
3.5. Aeration demand for biological reactions
3.5.1. Oxygen demand 3.5.2. Air supply
4. Design of membrane filtration system
4.1. Membrane flux and membrane area
4.2. Membrane aeration and cleaning
Typical parameters for
the design of MBR‐based
biological treatment of
municipal wastewater
Biological Wastewater Treatment
Online Course Series

## Slide 7: Biological treatment units
Two methods to calculate the volume of aerobic zone:
Option 1: calculate from nitrifying bacteria growth rate and SRT;
Option 2: calculate from ammonia utilization rate and N mass balance.
Designing steps
1. Selection of process flow
2. Design of pretreatment/primary treatment
3. Design of biological treatment units
3.1. Selection of design parameters
3.2. Tank volumes
3.2.1. Aerobic zone (O) 3.2.2. Anoxic zone (A2) 3.2.3. Anaerobic zone (A1)
3.3. Recirculation flow rates
3.4. Excess sludge production
3.5. Aeration demand for biological reactions
3.5.1. Oxygen demand 3.5.2. Air supply
4. Design of membrane filtration system
4.1. Membrane flux and membrane area
4.2. Membrane aeration and cleaning
Note:
VOM1 = VO + VM1
Volume of aerobic zone
Volume of aerobic tank
Free volume of membrane tank
(w/o membrane cassette volume)
A1
A2
O
M
Biological Wastewater Treatment
Online Course Series

## Slide 8: Biological treatment units
Designing steps
1. Selection of process flow
2. Design of pretreatment/primary treatment
3. Design of biological treatment units
3.1. Selection of design parameters
3.2. Tank volumes
3.2.1. Aerobic zone (O) 3.2.2. Anoxic zone (A2) 3.2.3. Anaerobic zone (A1)
3.3. Recirculation flow rates
3.4. Excess sludge production
3.5. Aeration demand for biological reactions
3.5.1. Oxygen demand 3.5.2. Air supply
4. Design of membrane filtration system
4.1. Membrane flux and membrane area
4.2. Membrane aeration and cleaning
Two methods to calculate the volume of aerobic zone:
Option 1: calculate from nitrifying bacteria growth rate and SRT
flow rate
volume of aerobic zone
BOD5 in feed & effluent
observed yield of solids
MLSS concentration
sludge age
Minimum sludge age in the aerobic zone
safety factor (1.5-3)
specific growth rate of nitrifying bacteria
Growth rate =
sludge mass (VOM1XOM1)
sludge age (θOM1)
= substrate (Q*ΔS) * sludge yield (Yt)
Biological Wastewater Treatment
Online Course Series

## Slide 9: Biological treatment units
Designing steps
1. Selection of process flow
2. Design of pretreatment/primary treatment
3. Design of biological treatment units
3.1. Selection of design parameters
3.2. Tank volumes
3.2.1. Aerobic zone (O) 3.2.2. Anoxic zone (A2) 3.2.3. Anaerobic zone (A1)
3.3. Recirculation flow rates
3.4. Excess sludge production
3.5. Aeration demand for biological reactions
3.5.1. Oxygen demand 3.5.2. Air supply
4. Design of membrane filtration system
4.1. Membrane flux and membrane area
4.2. Membrane aeration and cleaning
Two methods to calculate the volume of aerobic zone:
Option 1: calculate from nitrifying bacteria growth rate and SRT
Growth rate =
sludge mass (VOM1XOM1)
sludge age (θOM1)
= substrate (Q*ΔS) * sludge yield (Yt)
Minimum sludge age in the aerobic zone
specific growth rate of nitrifying bacteria
safety factor (1.5-3)
specific growth rate of nitrifying bacteria
maximum specific growth rate
half-velocity constant
temperature correction
ammonia concentration in the aerobic zone
Monod’s relationship for bacteria growth
Biological Wastewater Treatment
Online Course Series

## Slide 10: Biological treatment units
Designing steps
1. Selection of process flow
2. Design of pretreatment/primary treatment
3. Design of biological treatment units
3.1. Selection of design parameters
3.2. Tank volumes
3.2.1. Aerobic zone (O) 3.2.2. Anoxic zone (A2) 3.2.3. Anaerobic zone (A1)
3.3. Recirculation flow rates
3.4. Excess sludge production
3.5. Aeration demand for biological reactions
3.5.1. Oxygen demand 3.5.2. Air supply
4. Design of membrane filtration system
4.1. Membrane flux and membrane area
4.2. Membrane aeration and cleaning
Two methods to calculate the volume of aerobic zone:
Option 2: calculate from ammonia utilization rate and N mass balance
Utilization rate = uptake from wastewater – discharge with sludge
(VOM1XOM1*vn)
(Q*ΔN)
(0.124*ΔXv)
volume of aerobic zone
flow rate
MLSS concentration
biomass discharge rate
Kjeldahl N in influent & effluent
Biomass discharge rate
= biomass ratio * sludge yield * BOD5 uptake
specific ammonia utilization rate
Biological Wastewater Treatment
Online Course Series

## Slide 11: Biological treatment units
Designing steps
1. Selection of process flow
2. Design of pretreatment/primary treatment
3. Design of biological treatment units
3.1. Selection of design parameters
3.2. Tank volumes
3.2.1. Aerobic zone (O) 3.2.2. Anoxic zone (A2) 3.2.3. Anaerobic zone (A1)
3.3. Recirculation flow rates
3.4. Excess sludge production
3.5. Aeration demand for biological reactions
3.5.1. Oxygen demand 3.5.2. Air supply
4. Design of membrane filtration system
4.1. Membrane flux and membrane area
4.2. Membrane aeration and cleaning
Two methods to calculate the volume of aerobic zone:
Option 2: calculate from ammonia utilization rate and N mass balance
volume of aerobic zone
flow rate
Kjeldahl N in influent & effluent
MLSS concentration
specific ammonia utilization rate
Specific ammonia utilization rate
= maximum rate * Monod’s expression
Utilization rate = uptake from wastewater – discharge with sludge
(VOM1XOM1*vn)
(Q*ΔN)
(0.124*ΔXv)
biomass discharge rate
Biological Wastewater Treatment
Online Course Series

## Slide 12: Biological treatment units
Two methods to calculate the volume of aerobic zone:
Designing steps
1. Selection of process flow
2. Design of pretreatment/primary treatment
3. Design of biological treatment units
3.1. Selection of design parameters
3.2. Tank volumes
3.2.1. Aerobic zone (O) 3.2.2. Anoxic zone (A2) 3.2.3. Anaerobic zone (A1)
3.3. Recirculation flow rates
3.4. Excess sludge production
3.5. Aeration demand for biological reactions
3.5.1. Oxygen demand 3.5.2. Air supply
4. Design of membrane filtration system
4.1. Membrane flux and membrane area
4.2. Membrane aeration and cleaning
Option 1: from nitrifying bacteria growth rate and SRT
Option 2: from ammonia utilization rate and N mass balance
A1
A2
O
M
Biological Wastewater Treatment
Online Course Series

## Slide 13: Biological treatment units
Volume of anoxic zone (A2) calculated from denitrification rate and N mass balance:
Designing steps
1. Selection of process flow
2. Design of pretreatment/primary treatment
3. Design of biological treatment units
3.1. Selection of design parameters
3.2. Tank volumes
3.2.1. Aerobic zone (O) 3.2.2. Anoxic zone (A2) 3.2.3. Anaerobic zone (A1)
3.3. Recirculation flow rates
3.4. Excess sludge production
3.5. Aeration demand for biological reactions
3.5.1. Oxygen demand 3.5.2. Air supply
4. Design of membrane filtration system
4.1. Membrane flux and membrane area
4.2. Membrane aeration and cleaning
Denitrification rate = uptake from wastewater – discharge with sludge
(VA2XA2*Kdn)
(Q*ΔN)
(0.124*ΔXv)
TN in influent & effluent
biomass discharge rate
MLSS concentration
volume of anoxic zone
specific denitrification rate
0.03-0.06 kgNO3--N/(kgMLSS·d)
temperature correction
A1
A2
O
M
Biological Wastewater Treatment
Online Course Series

## Slide 14: Biological treatment units
Volume of anaerobic zone (A1) empirically calculated from HRT:
Designing steps
1. Selection of process flow
2. Design of pretreatment/primary treatment
3. Design of biological treatment units
3.1. Selection of design parameters
3.2. Tank volumes
3.2.1. Aerobic zone (O) 3.2.2. Anoxic zone (A2) 3.2.3. Anaerobic zone (A1)
3.3. Recirculation flow rates
3.4. Excess sludge production
3.5. Aeration demand for biological reactions
3.5.1. Oxygen demand 3.5.2. Air supply
4. Design of membrane filtration system
4.1. Membrane flux and membrane area
4.2. Membrane aeration and cleaning
flow rate
hydraulic retention time (HRT) of anaerobic zone
volume of anaerobic zone
(normally 1-2 h)
A1
A2
O
M
Biological Wastewater Treatment
Online Course Series

## Slide 15: Biological treatment units
Designing steps
1. Selection of process flow
2. Design of pretreatment/primary treatment
3. Design of biological treatment units
3.1. Selection of design parameters
3.2. Tank volumes
3.2.1. Aerobic zone (O) 3.2.2. Anoxic zone (A2) 3.2.3. Anaerobic zone (A1)
3.3. Recirculation flow rates
3.4. Excess sludge production
3.5. Aeration demand for biological reactions
3.5.1. Oxygen demand 3.5.2. Air supply
4. Design of membrane filtration system
4.1. Membrane flux and membrane area
4.2. Membrane aeration and cleaning
#1 recirculation ratio RA2→A1
(typically 1-2)
#2 recirculation ratio RO→A2
(typically 3-5)
A1
A2
O
M
#3 recirculation ratio RM→O
(typically 4-6)
Excess sludge
Biological Wastewater Treatment
Online Course Series

## Slide 16: Biological treatment units
Designing steps
1. Selection of process flow
2. Design of pretreatment/primary treatment
3. Design of biological treatment units
3.1. Selection of design parameters
3.2. Tank volumes
3.2.1. Aerobic zone (O) 3.2.2. Anoxic zone (A2) 3.2.3. Anaerobic zone (A1)
3.3. Recirculation flow rates
3.4. Excess sludge production
3.5. Aeration demand for biological reactions
3.5.1. Oxygen demand 3.5.2. Air supply
4. Design of membrane filtration system
4.1. Membrane flux and membrane area
4.2. Membrane aeration and cleaning
#1 recirculation ratio RA2→A1
(typically 1-2)
#2 recirculation ratio RO→A2
(typically 3-5)
A1
A2
O
M
#3 recirculation ratio RM→O
(typically 4-6)
Excess sludge
Mixed liquor concentrations according to mass balance:
Decreasing
Biological Wastewater Treatment
Online Course Series

## Slide 17: Biological treatment units
Designing steps
1. Selection of process flow
2. Design of pretreatment/primary treatment
3. Design of biological treatment units
3.1. Selection of design parameters
3.2. Tank volumes
3.2.1. Aerobic zone (O) 3.2.2. Anoxic zone (A2) 3.2.3. Anaerobic zone (A1)
3.3. Recirculation flow rates
3.4. Excess sludge production
3.5. Aeration demand for biological reactions
3.5.1. Oxygen demand 3.5.2. Air supply
4. Design of membrane filtration system
4.1. Membrane flux and membrane area
4.2. Membrane aeration and cleaning
#1 recirculation ratio RA2→A1
(typically 1-2)
#2 recirculation ratio RO→A2
(typically 3-5)
A1
A2
O
M
#3 recirculation ratio RM→O
(typically 4-6)
Excess sludge
Recirculation flow rates:
Biological Wastewater Treatment
Online Course Series

## Slide 18: Biological treatment units
Designing steps
1. Selection of process flow
2. Design of pretreatment/primary treatment
3. Design of biological treatment units
3.1. Selection of design parameters
3.2. Tank volumes
3.2.1. Aerobic zone (O) 3.2.2. Anoxic zone (A2) 3.2.3. Anaerobic zone (A1)
3.3. Recirculation flow rates
3.4. Excess sludge production
3.5. Aeration demand for biological reactions
3.5.1. Oxygen demand 3.5.2. Air supply
4. Design of membrane filtration system
4.1. Membrane flux and membrane area
4.2. Membrane aeration and cleaning
Three options to calculate the excess sludge production rate:
Option 1: from synthesis yield of biomass (for rigorous calculation)
excess sludge production rate
synthesis from BOD5
endogenous decay
conversion from influent SS
Y –– synthesis yield of biomass (0.3-0.6 kgMLVSS/kgBOD5)
kd –– endogenous decay coefficient (0.05-0.2 d-1)
y –– MLVSS/MLSS ratio (0.4-0.7 kgMLVSS/kgMLSS)
f –– conversion rate of sludge from SS (0.5-0.7 gMLSS/gSS)
Biological Wastewater Treatment
Online Course Series

## Slide 19: Biological treatment units
Designing steps
1. Selection of process flow
2. Design of pretreatment/primary treatment
3. Design of biological treatment units
3.1. Selection of design parameters
3.2. Tank volumes
3.2.1. Aerobic zone (O) 3.2.2. Anoxic zone (A2) 3.2.3. Anaerobic zone (A1)
3.3. Recirculation flow rates
3.4. Excess sludge production
3.5. Aeration demand for biological reactions
3.5.1. Oxygen demand 3.5.2. Air supply
4. Design of membrane filtration system
4.1. Membrane flux and membrane area
4.2. Membrane aeration and cleaning
Three options to calculate the excess sludge production rate:
Option 1: from synthesis yield of biomass (for rigorous calculation)
excess sludge production rate
synthesis from BOD5
endogenous decay
conversion from influent SS
Option 2: from observed yield of solids (for convenient estimation)
Option 3: from total sludge age (for retrospective analysis)
average MLSS
concentration
empirical yield from BOD5
Yt =
0.25-0.45 kgMLSS/kgBOD5 (with primary sedimentation)
or 0.5-0.9 kgMLSS/kgBOD5
(w/o primary sedimentation)
total sludge age (SRT)
typically 15-30 d for MBR
Biological Wastewater Treatment
Online Course Series

## Slide 20: Biological treatment units
Designing steps
1. Selection of process flow
2. Design of pretreatment/primary treatment
3. Design of biological treatment units
3.1. Selection of design parameters
3.2. Tank volumes
3.2.1. Aerobic zone (O) 3.2.2. Anoxic zone (A2) 3.2.3. Anaerobic zone (A1)
3.3. Recirculation flow rates
3.4. Excess sludge production
3.5. Aeration demand for biological reactions
3.5.1. Oxygen demand 3.5.2. Air supply
4. Design of membrane filtration system
4.1. Membrane flux and membrane area
4.2. Membrane aeration and cleaning
Three options to calculate the excess sludge production rate:
When Al or Fe salts are added for TP removal or membrane fouling control,
additional amount of excess sludge is estimated to be 5*Al or 3.5*Fe
Option 1
Option 2
Option 3
Flow rate for excess sludge discharge
(pumped from membrane tank):
MLSS concentration
of membrane tank
Biological Wastewater Treatment
Online Course Series

## Slide 21: Biological treatment units
Designing steps
1. Selection of process flow
2. Design of pretreatment/primary treatment
3. Design of biological treatment units
3.1. Selection of design parameters
3.2. Tank volumes
3.2.1. Aerobic zone (O) 3.2.2. Anoxic zone (A2) 3.2.3. Anaerobic zone (A1)
3.3. Recirculation flow rates
3.4. Excess sludge production
3.5. Aeration demand for biological reactions
3.5.1. Oxygen demand 3.5.2. Air supply
4. Design of membrane filtration system
4.1. Membrane flux and membrane area
4.2. Membrane aeration and cleaning
DO offset
BOD offset
demand for oxidizing organic carbon
demand for nitrification
offset for denitrification
supplement by recirculation from membrane tank
Net oxygen demand:
VO –– volume of aerobic tank
VM1 –– free volume of membrane tank
Net oxygen demand
Biological Wastewater Treatment
Online Course Series

## Slide 22: Biological treatment units
Designing steps
1. Selection of process flow
2. Design of pretreatment/primary treatment
3. Design of biological treatment units
3.1. Selection of design parameters
3.2. Tank volumes
3.2.1. Aerobic zone (O) 3.2.2. Anoxic zone (A2) 3.2.3. Anaerobic zone (A1)
3.3. Recirculation flow rates
3.4. Excess sludge production
3.5. Aeration demand for biological reactions
3.5.1. Oxygen demand 3.5.2. Air supply
4. Design of membrane filtration system
4.1. Membrane flux and membrane area
4.2. Membrane aeration and cleaning
DO offset
BOD offset
demand for oxidizing organic carbon
demand for nitrification
offset for denitrification
supplement by recirculation from membrane tank
Net oxygen demand:
Oxygen demand for oxidizing organic carbon
offset for biomass synthesis
consumption for BOD removal
Net oxygen demand
Biological Wastewater Treatment
Online Course Series

## Slide 23: Biological treatment units
Designing steps
1. Selection of process flow
2. Design of pretreatment/primary treatment
3. Design of biological treatment units
3.1. Selection of design parameters
3.2. Tank volumes
3.2.1. Aerobic zone (O) 3.2.2. Anoxic zone (A2) 3.2.3. Anaerobic zone (A1)
3.3. Recirculation flow rates
3.4. Excess sludge production
3.5. Aeration demand for biological reactions
3.5.1. Oxygen demand 3.5.2. Air supply
4. Design of membrane filtration system
4.1. Membrane flux and membrane area
4.2. Membrane aeration and cleaning
DO offset
BOD offset
demand for oxidizing organic carbon
demand for nitrification
offset for denitrification
supplement by recirculation from membrane tank
Net oxygen demand:
Oxygen demand for nitrification
offset for biomass synthesis
consumption for nitrification
Net oxygen demand
Biological Wastewater Treatment
Online Course Series

## Slide 24: Biological treatment units
DO offset
BOD offset
demand for oxidizing organic carbon
demand for nitrification
offset for denitrification
supplement by recirculation from membrane tank
Net oxygen demand:
Oxygen demand offset for denitrification
offset for biomass synthesis
oxygen equivalent for denitrification
Net oxygen demand
Biological Wastewater Treatment
Online Course Series
Designing steps
1. Selection of process flow
2. Design of pretreatment/primary treatment
3. Design of biological treatment units
3.1. Selection of design parameters
3.2. Tank volumes
3.2.1. Aerobic zone (O) 3.2.2. Anoxic zone (A2) 3.2.3. Anaerobic zone (A1)
3.3. Recirculation flow rates
3.4. Excess sludge production
3.5. Aeration demand for biological reactions
3.5.1. Oxygen demand 3.5.2. Air supply
4. Design of membrane filtration system
4.1. Membrane flux and membrane area
4.2. Membrane aeration and cleaning

## Slide 25: Biological treatment units
Net oxygen demand
DO offset
BOD offset
demand for oxidizing organic carbon
demand for nitrification
offset for denitrification
supplement by recirculation from membrane tank
Net oxygen demand:
Oxygen demand offset for recirculation
DO in the recirculated flow (4-8 mg/L)
Biological Wastewater Treatment
Online Course Series
Designing steps
1. Selection of process flow
2. Design of pretreatment/primary treatment
3. Design of biological treatment units
3.1. Selection of design parameters
3.2. Tank volumes
3.2.1. Aerobic zone (O) 3.2.2. Anoxic zone (A2) 3.2.3. Anaerobic zone (A1)
3.3. Recirculation flow rates
3.4. Excess sludge production
3.5. Aeration demand for biological reactions
3.5.1. Oxygen demand 3.5.2. Air supply
4. Design of membrane filtration system
4.1. Membrane flux and membrane area
4.2. Membrane aeration and cleaning

## Slide 26: Biological treatment units
Net oxygen demand
DO offset
BOD offset
Convert the net oxygen demand (O) to standard-state demand (Ostd)
(at 20 °C and 1 bar in clean water)
temperature correction
α –– ratio of oxygen transfer coefficient in sludge vs in clean water
β –– ratio of saturated DO concentration in sludge vs in clean water
saturated DO
background DO
pressure correction
sludge vs clean water correction
Biological Wastewater Treatment
Online Course Series
Designing steps
1. Selection of process flow
2. Design of pretreatment/primary treatment
3. Design of biological treatment units
3.1. Selection of design parameters
3.2. Tank volumes
3.2.1. Aerobic zone (O) 3.2.2. Anoxic zone (A2) 3.2.3. Anaerobic zone (A1)
3.3. Recirculation flow rates
3.4. Excess sludge production
3.5. Aeration demand for biological reactions
3.5.1. Oxygen demand 3.5.2. Air supply
4. Design of membrane filtration system
4.1. Membrane flux and membrane area
4.2. Membrane aeration and cleaning

## Slide 27: Biological treatment units
Designing steps
1. Selection of process flow
2. Design of pretreatment/primary treatment
3. Design of biological treatment units
3.1. Selection of design parameters
3.2. Tank volumes
3.2.1. Aerobic zone (O) 3.2.2. Anoxic zone (A2) 3.2.3. Anaerobic zone (A1)
3.3. Recirculation flow rates
3.4. Excess sludge production
3.5. Aeration demand for biological reactions
3.5.1. Oxygen demand 3.5.2. Air supply
4. Design of membrane filtration system
4.1. Membrane flux and membrane area
4.2. Membrane aeration and cleaning
Net oxygen demand
DO offset
BOD offset
The α factor: an important correction for oxygen mass transfer in sludge
(generally larger in MBR than in CAS)
empirical parameter, ~1.7
empirical, ~0.08
MLSS in the aerobic tank
Image source: Xu et al. Evaluating oxygen mass transfer parameters for large-scale engineering application of membrane bioreactors. Process Biochemistry, 2017 (60):13-18.
Biological Wastewater Treatment
Online Course Series

## Slide 28: Biological treatment units
Designing steps
1. Selection of process flow
2. Design of pretreatment/primary treatment
3. Design of biological treatment units
3.1. Selection of design parameters
3.2. Tank volumes
3.2.1. Aerobic zone (O) 3.2.2. Anoxic zone (A2) 3.2.3. Anaerobic zone (A1)
3.3. Recirculation flow rates
3.4. Excess sludge production
3.5. Aeration demand for biological reactions
3.5.1. Oxygen demand 3.5.2. Air supply
4. Design of membrane filtration system
4.1. Membrane flux and membrane area
4.2. Membrane aeration and cleaning
Calculate the operational air supply (GO) from oxygen demand (Ostd) according to aerator efficiency (blower or mechanical aerator):
For blower aeration:
standard-state oxygen demand
standard-state air supply
aeration efficiency
oxygen content in air
Biological Wastewater Treatment
Online Course Series

## Slide 29: Biological treatment units
Designing steps
1. Selection of process flow
2. Design of pretreatment/primary treatment
3. Design of biological treatment units
3.1. Selection of design parameters
3.2. Tank volumes
3.2.1. Aerobic zone (O) 3.2.2. Anoxic zone (A2) 3.2.3. Anaerobic zone (A1)
3.3. Recirculation flow rates
3.4. Excess sludge production
3.5. Aeration demand for biological reactions
3.5.1. Oxygen demand 3.5.2. Air supply
4. Design of membrane filtration system
4.1. Membrane flux and membrane area
4.2. Membrane aeration and cleaning
An example of AAO-MBR
A2
O
M
Summary:
Volume of the tanks
Mixed liquor recirculation ratios
Excess sludge production
Aeration demand
A1
Biological Wastewater Treatment
Online Course Series