## Slide 1
Course on Membrane Bioreactors
MBR plant design, O&M:
Membrane Filtration
System
Kang Xiao

## Slide 2: Contents
  Process composition
  Pretreatment
  Biological treatment units
  Membrane filtration system
Biological Wastewater Treatment
Online Course Series

## Slide 3: Membrane filtration system
Designing steps
1. Selection of process flow
2. Design of pretreatment/primary treatment
3. Design of biological treatment units
3.1. Selection of design parameters
3.2. Tank volumes
3.2.1. Aerobic zone (O) 3.2.2. Anoxic zone (A2) 3.2.3. Anaerobic zone (A1)
3.3. Recirculation flow rates
3.4. Excess sludge production
3.5. Aeration demand for biological reactions
3.5.1. Oxygen demand 3.5.2. Air supply
4. Design of membrane filtration system
4.1. Membrane flux and membrane area
4.2. Membrane aeration and cleaning
A1
A2
O
M
Membrane flux
Membrane aeration
Membrane cleaning
Membrane area
Submerged
Side-stream
Biological Wastewater Treatment
Online Course Series

## Slide 4: Membrane filtration system
Membrane flux
Membrane area
Membrane aeration
Membrane cleaning
The average flux is maintained relatively constant during the filtration.
Constant-flux filtration mode
Time
Flux
Pressure
Time
Intermittent operation manner
The suction pumps are operated in an on/off intermittent manner to impede fouling development.
A filtration cycle consists of a running period (e.g. 7-13 min) and a relaxation period (e.g. 1-3 min).
Backwash requirement (optional)
For side-stream MBRs, the membrane should be back-flushed at appropriate frequency, duration and intensity.
Biological Wastewater Treatment
Online Course Series

## Slide 5: Membrane filtration system
Membrane flux
Membrane area
Membrane aeration
Membrane cleaning
Time
Flux
Running flux (J1)
Average flux (Javg)
running period
relaxation period
Running flux
The instantaneous flux in the running period (e.g. 7-13 min) of a filtration cycle.
Average flux
Weighted average of the fluxes in the running (7-13 min) and relaxation period (1-3 min) of a filtration cycle.
Normally 15-25 LMH for submerged MBRs and 30-45 LMH for side-stream MBRs for municipal wastewater.
Biological Wastewater Treatment
Online Course Series

## Slide 6: Membrane filtration system
Membrane flux
Membrane area
Membrane aeration
Membrane cleaning
Time
Flux
Average flux (with backwash)
The reverse flux for backwash subtracted from average of flux subtracted from the average flux.
Running flux (J1)
Average flux (Javg)
backwash flux
backwash interval
Running flux
The instantaneous flux in the running period (e.g. 7-13 min) of a filtration cycle.
Average flux
Weighted average of the fluxes in the running (7-13 min) and relaxation period (1-3 min) of a filtration cycle.
Normally 15-25 LMH for submerged MBRs and 30-45 LMH for side-stream MBRs for municipal wastewater.
backwash duration
Avg with backwash
Biological Wastewater Treatment
Online Course Series

## Slide 7: Membrane filtration system
Membrane flux
Membrane area
Membrane aeration
Membrane cleaning
Critical flux
The threshold for slow/rapid fouling development. Operation above critical flux will lead to severe fouling.
Peak flux
Corresponds to the peak flow rate of the wastewater influent.
Temporary peak flux
When some of the membrane cassettes are suspended for membrane cleaning and equipment maintenance,
the other membrane cassettes will sustain temporarily high flux.
Flux
Fouling
(resistance)
Critical flux
Sub-critical
Super-critical
Severe fouling
Biological Wastewater Treatment
Online Course Series

## Slide 8: Membrane filtration system
Membrane flux
Membrane aeration
Membrane cleaning
Total volume of membrane tank (VM, m3)
Total membrane area (AM, m2)
Number of membrane cassettes (nM)
Membrane area
total flow rate (m3/d)
average flux (L/m2·h)
safety factor, approximately 1.1-1.2
membrane area
per unit cassette (m2)
apparent packing density of the whole membrane tank (m2/m3)
…
Biological Wastewater Treatment
Online Course Series

## Slide 9: Membrane filtration system
Membrane flux
Membrane cleaning
Membrane area
Membrane aeration
Air scouring to mitigate membrane fouling and clogging
In submerged MBRs, coarse-bubble aeration is normally applied for this purpose.
Specific aeration demand (SAD)
specific aeration demand with respect to membrane cassette footprint
SADf
60-120 Nm3/m2·h
specific aeration demand with respect to membrane area
SADm
specific aeration demand with respect to permeate flow amount
SADp
0.3 Nm3/m2·h for hollow-fiber
0.6 Nm3/m2·h for flat-sheet
15 Nm3/m3-permeate for hollow-fiber
30 Nm3/m3-permeate for flat-sheet
Air supply for membrane aeration
Biological Wastewater Treatment
Online Course Series
Submerged MBRs

## Slide 10: Membrane filtration system
Membrane flux
Membrane cleaning
Membrane area
Membrane aeration
Air scouring to mitigate membrane fouling and clogging
In submerged MBRs, coarse-bubble aeration is normally applied for this purpose.
Specific aeration demand (SAD)
specific aeration demand with respect to membrane cassette footprint
SADf
60-120 Nm3/m2·h
specific aeration demand with respect to membrane area
SADm
specific aeration demand with respect to permeate flow amount
SADp
0.3 Nm3/m2·h for hollow-fiber
0.6 Nm3/m2·h for flat-sheet
15 Nm3/m3-permeate for hollow-fiber
30 Nm3/m3-permeate for flat-sheet
Air supply for membrane aeration
total footprint of the membrane cassettes (m2)
total membrane area (m2)
total permeate flow rate (m3/d)
air supply to the membrane tank (Nm3/h)
Biological Wastewater Treatment
Online Course Series
submerged MBRs

## Slide 11: Membrane filtration system
Membrane flux
Membrane area
Membrane aeration
Membrane cleaning
CIA, cleaning in air
CIP, cleaning in place
CEB, chemically enhanced backwash
recovery cleaning
in situ cleaning
ex situ cleaning
maintenance cleaning
recovery cleaning
Chemical cleaning modes
Includes in situ cleaning and ex situ cleaning according to the location of the cleaning,
or maintenance cleaning and recovery cleaning according to the severity of fouling.
In situ
Ex situ
Wang et al. Membrane cleaning in membrane bioreactors: A review. Journal of Membrane Science, 2014, 468: 276-307.
Biological Wastewater Treatment
Online Course Series

## Slide 12: Membrane filtration system
Membrane flux
Membrane area
Membrane aeration
Membrane cleaning
CIA, cleaning in air
CIP, cleaning in place
CEB, chemically enhanced backwash
recovery cleaning
in situ cleaning
ex situ cleaning
maintenance cleaning
recovery cleaning
Chemical cleaning modes
Includes in situ cleaning and ex situ cleaning according to the location of the cleaning,
or maintenance cleaning and recovery cleaning according to the severity of fouling.
In situ
Ex situ
Wang et al. Membrane cleaning in membrane bioreactors: A review. Journal of Membrane Science, 2014, 468: 276-307.
Biological Wastewater Treatment
Online Course Series

## Slide 13: Membrane filtration system
Membrane flux
Membrane area
Membrane aeration
Membrane cleaning
Chemical cleaning procedures and conditions
Type | Module | Frequency | Procedure | Dosage
Maintenance cleaning | Hollow fiber | Weekly | Injection (30 min) → immersion (60 min) → aeration (30 min) | NaOCl concentration: 0.5-1.0 g/L of chlorine; Dosing volume: 3-5 L/m2
 | Flat sheet | Not mandatory (depending on the manufacturer) |  | 
Intensified cleaning | Hollow fiber | Monthly, or when TMP > 30 kPa | Injection (30 min) → immersion (60 min) → aeration (30 min) | NaOCl concentration: 2-3 g/L of chlorine; Dosing volume: 3-5 L/m2
 | Flat sheet | Once every 3-6 months, or when TMP > 30 kPa | Injection (8-15 min) → immersion (1-2 h) | NaOCl concentration: 3-5 g/L of chlorine; Dosing volume: 4-6 L/m2
Recovery cleaning | Hollow fiber and flat sheet | Regularly once a year, immediately when TMP ≥ 50 kPa (or when online cleaning fails to keep TMP < 30 kPa) | Immersed in NaOCl (3-5 g/L of chlorine) for 12-24 h, or immersed in NaOCl (3-5 g/L of chlorine) and citric/oxalic acid (10-20 g/L) alternately | 
Biological Wastewater Treatment
Online Course Series

## Slide 14: Membrane filtration system
Membrane flux
Membrane area
Membrane aeration
Membrane cleaning
Chemical cleaning procedures and conditions
Type | Module | Frequency | Procedure | Dosage
Maintenance cleaning | Hollow fiber | Weekly | Injection (30 min) → immersion (60 min) → aeration (30 min) | NaOCl concentration: 0.5-1.0 g/L of chlorine; Dosing volume: 3-5 L/m2
 | Flat sheet | Not mandatory (depending on the manufacturer) |  | 
Intensified cleaning | Hollow fiber | Monthly, or when TMP > 30 kPa | Injection (30 min) → immersion (60 min) → aeration (30 min) | NaOCl concentration: 2-3 g/L of chlorine; Dosing volume: 3-5 L/m2
 | Flat sheet | Once every 3-6 months, or when TMP > 30 kPa | Injection (8-15 min) → immersion (1-2 h) | NaOCl concentration: 3-5 g/L of chlorine; Dosing volume: 4-6 L/m2
Recovery cleaning | Hollow fiber and flat sheet | Regularly once a year, immediately when TMP ≥ 50 kPa (or when online cleaning fails to keep TMP < 30 kPa) | Immersed in NaOCl (3-5 g/L of chlorine) for 12-24 h, or immersed in NaOCl (3-5 g/L of chlorine) and citric/oxalic acid (10-20 g/L) alternately | 
Biological Wastewater Treatment
Online Course Series

## Slide 15: Membrane filtration system
Membrane flux
Membrane area
Membrane aeration
Membrane cleaning
Chemical cleaning procedures and conditions
Type | Module | Frequency | Procedure | Dosage
Maintenance cleaning | Hollow fiber | Weekly | Injection (30 min) → immersion (60 min) → aeration (30 min) | NaOCl concentration: 0.5-1.0 g/L of chlorine; Dosing volume: 3-5 L/m2
 | Flat sheet | Not mandatory (depending on the manufacturer) |  | 
Intensified cleaning | Hollow fiber | Monthly, or when TMP > 30 kPa | Injection (30 min) → immersion (60 min) → aeration (30 min) | NaOCl concentration: 2-3 g/L of chlorine; Dosing volume: 3-5 L/m2
 | Flat sheet | Once every 3-6 months, or when TMP > 30 kPa | Injection (8-15 min) → immersion (1-2 h) | NaOCl concentration: 3-5 g/L of chlorine; Dosing volume: 4-6 L/m2
Recovery cleaning | Hollow fiber and flat sheet | Regularly once a year, immediately when TMP ≥ 50 kPa (or when online cleaning fails to keep TMP < 30 kPa) | Immersed in NaOCl (3-5 g/L of chlorine) for 12-24 h, or immersed in NaOCl (3-5 g/L of chlorine) and citric/oxalic acid (10-20 g/L) alternately | 
Biological Wastewater Treatment
Online Course Series

## Slide 16: Membrane filtration system
Membrane flux
Membrane area
Membrane aeration
Membrane cleaning
Filtration cycle
Intermittent mode
Different fluxes
Running flux
Average flux
Peak flux
Temporary peak flux
Critical flux
Total area
Cassette number
Membrane tank volume
Chemical cleaning specifications
In situ cleaning
Ex situ cleaning
Maintenance cleaning
Intensified cleaning
Recovery cleaning
Cleaning conditions
Frequency
Dosage
Avg
Coarse-bubble scouring
Specific aeration demand (SAD)
SADf
SADm
SADp
Biological Wastewater Treatment
Online Course Series