## Slide 1
Course on Membrane Bioreactors
Practical Applications
- Part 1
Jiao Zhang
Notes: Hello everyone! I’m Jiao Zhang from Tsinghua University. In this Case study section, we are going to review several practical applications of MBR technology, which could help you better understand its usage and the effect in the whole treatment process.

## Slide 2: Contents
  Overall practical application
  Case study 1: A large-scale underground MBR for municipal wastewater treatment
  Case study 2: MBRs for municipal wastewater treatment with no recovery cleaning and low energy consumption
  Case study 3
  Case study 4
  Case study 5
Biological Wastewater Treatment
Online Course Series
Notes: We’ve had lots of engineering application of MBR technologies around the world. In this section, we’ll have a glance of the overall features of these practical applications, and several cases for different wastewater will be introduced.

## Slide 3: Overall practical application
  MBR applications
    Water sectors: municipal wastewater, industrial wastewater, leachate
    Advantages: steady effluent quality, small footprint (esp. underground),
    Feasible modification in application: refractory pollutants, nutrients, energy reduction…
Recycling
Discharge
Biological Wastewater Treatment
Online Course Series
Notes: The effluent requirements and standards are increasingly stringent. MBRs have been extensively applied to treat municipal wastewater, industrial wastewater and leachate taking the advantages of steady effluent quality, small footprint, which is especially favourable in urban area, etc. Most MBRs, especially large-scale applications, are for municipal wastewater treatment. Modification of treatment processes with MBRs are feasible in application according to the influent characteristics and water quality standards. For example, industrial wastewater always contains refractory pollutants to be removed, the nutrient salts in municipal wastewater need to be lowered down to a designated level, and there are some modifications to reduce the energy consumption of the whole treatment process. The treated water of MBRs are discharged into natural water body, or reused in municipal and industrial sectors.

## Slide 4
  Globally increasing application of MBR technology
    62 largest MBRs (capacity > 105 m3/d) totally treat 147.33 x 105 m3/d wastewater
    China has a large market share of large-scale MBRs in the world
Geo-distribution of global largest MBRs
according to average daily flow
Development of MBRs for municipal wastewater treatment in China
(individual treatment capacity ≥ 105 m3/d)
Overall practical application
Biological Wastewater Treatment
Online Course Series
Source: (1) The MBR site: https://www.thembrsite.com/ . (2) Jiao Zhang, et al., Environmental Engineering, 2022, 40( 3):1-6,153 (in Chinese)．
Notes: There have been significant increases in the treatment capacity of full-scale MBRs. According to the MBR site, the global number of the largest MBRs with a treatment capacity of ≥ 105 m3/d has reached 62 with a total peak treatment capacity of 147.33·105
m3/d. China, USA, and Singapore have most of the largest MBRs, with 84 % of the total global treatment capacity.
It is noteworthy that China has the largest share of large-scale MBRs. Taking municipal wastewater treatment as an example, the first large-scale MBR in China was commissioned in 2006, and till 2020, there have been amolst 300 large-scale MBRs, with a total treatment capacity of more than 1.7 X 10^7 m3/d. Among these MBRs, about 1/3 of them are constructed under ground. The underground construction is friendly to areas with limited available land.

## Slide 5: Contents
  Overall practical application
  Case study 1: A large-scale underground MBR for municipal wastewater treatment
  Case study 2: MBRs for municipal wastewater treatment with no recovery cleaning and low energy consumption
  Case study 3
  Case study 4
  Case study 5
Biological Wastewater Treatment
Online Course Series
Notes: Next, we’ll look at several MBR cases. The influent in these cases includes municipal wastewater, industrial wastewater, and
leachate.

## Slide 6: Case study 1: Jingxi Wastewater Treatment Plant
  Info of Jingxi plant
    Location: Guangzhou, China
    Commissioning time: 2010
    Catchment area of 16,500 ha
    Capacity: 100,000 m3/d (peak: 120,000 m3/d)
    Footprint: 1.82 ha
A large-scale underground MBR for municipal wastewater treatment
Biological Wastewater Treatment
Online Course Series
Notes: The first one is Jingxi Wastewater Treatment Plant. We may call it Jingxi Plant. It is in Guangzhou, a southern city in China. It’s a large-scale underground MBR for municipal wastewater treatment. It was commissioned in 2010. It has a treatment capacity of 100,000 m3/d (peak flow at 120,000 m3/d), occupying a footprint of 1.82 ha and treating wastewater from a catchment area of 16,500 ha. It was the largest underground MBR plant in Asia when it was commissioned.
It was mentioned that this plant is under ground. We can see the pleasant landscape of this plant. The synergy between
the smaller footprint due to MBR technology and underground placement of the plant also significantly reduced the capital expenditure on land investment as rapid urbanization has greatly driven up land prices in Guangzhou.

## Slide 7: Case study 1: Jingxi Wastewater Treatment Plant
  Treatment process: AAO-MBR
TN & TP removal
HRT: 1.03 h, 2.09 h , 3.00 h
Biological Wastewater Treatment
Online Course Series
AAO: Anaerobic-Anoxic-Aerobic. | HRT: Hydraulic retention time. | TN: Total nitrogen. | TP: Total phosphorus.
Notes: At Jingxi underground WWTP the influent flows into the AAO-MBR system after primary treatment by a fine screen and grit chamber.
The AAO process guarantees the removal efficiencies of TN and TP (with the aid of chemical coagulants). The HRT of each tank in the AAO-MBR system is set at 1.03 h, 2.09 h, 3 h and 1.24 h, respectively. Following the AAO tanks is the membrane tank. Then, the plant effluent is discharged to replenish the nearby urban river.

## Slide 8: Case study 1: Jingxi Wastewater Treatment Plant
Submerged MBRs
PVDF hollow fiber membrane
88 modules 🡪 1 unit (1760 m2 area)
20 units/tank × 10 tanks
  Treatment process: AAO-MBR
Biological Wastewater Treatment
Online Course Series
Notes: Regarding the membrane tank, it is a submerged MBR. PVDF hollow fibre membranes from Memstar is adopted.
88 membrane modules as a unit, the total effective surface area of each membrane unit is 1,760 m2. In one membrane tank, there are 20 units, and in the plant, ten membrane tanks are operated simultaneously.

## Slide 9: Case study 1: Jingxi Wastewater Treatment Plant
MLSS: Mixed liquor suspended solids. | SRT: Sludge retention time.
Flux: 15 ~ 25 L/m2·h
HRT: 1.24 h
MLSS: 8,000~13,000 mg/L
SRT: 12 d
Energy demand: 0.18~ 0.22 kWh/m3
  Treatment process: AAO-MBR
Biological Wastewater Treatment
Online Course Series
Notes: The baseline flux is 15 l/m2.h, and higher flux up to 25 l/m2.h can be achieved with intensified membrane maintenance cleaning protocols.
MLSS in the membrane tank is in the range of 8,000-13,000 mg/l, and SRT is controlled at 12 d.
The specific energy demand of the system can be reduced from 0.22 kWh/m3 to 0.18 kWh/m3 by the optimized internal recirculation path and aeration protocol.

## Slide 10: Case study 1: Jingxi Wastewater Treatment Plant
Quality (mg/L)
BOD5 = 3
COD = 13
SS = 2
NH4+-N = 0.6
TN = 7.4
TP = 0.15
  Treatment process: AAO-MBR
Quality (mg/L)
BOD5 = 130
COD = 210
SS = 90
NH4+-N = 20
TN = 30
TP = 2.5
Biological Wastewater Treatment
Online Course Series
Notes: The influent has a COD concentration of 210 mg/L, ammonia 20, TN 30 and TP 2.5. After the treatment process, the effluent of MBR tank has a COD of 13 mg/L, approximately 94% was removed. The ammonia was 0.6 mg.L, TN 7.4 and TP 0.15, which can meet the standards for river replenishing.

## Slide 11: Case study 2: Tuas Water Reclamation Plant
  Info of Tuas Water Reclamation Plant
    Location: Singapore
    Commissioning time: by 2025
    Capacity: 800,000 m3/d (peak: 1,200,000 m3/d)
    It would be the world’s largest MBR then
Source: https://www.pub.gov.sg/dtss/phase2/twrp
MBRs for municipal wastewater treatment
with low energy consumption and no chemical-recovery cleaning
  An Integrated Validation and Demonstration Plant
    Commissioning time: 2017
    Capacity: 12,500 m3/d (peak: 18,7500 m3/d)
Biological Wastewater Treatment
Online Course Series
Notes: Singapore is an area intensively appling MBR technologies in wastewater treatment. There are seven MBRs in operation or under commission in Singapore. The total treatment capacity is 328,050 m3/d, and the total peak flow is 522,075 m3/d. It is worthy to be addressed that one of the largest MBRs worldwide is under construction in Singapore, named Tuas Water Reclamation Plant. It is designed to have an average capacity of 800,000 m3/d, peak flow 1,200,000 m3/d.
Before the construction, an Integrated Validation and Demonstration Plant was commissioned in 2017, with a treatment capacity of 12,500 m3/d (peak 18,750 m3/d). It simulates the treatment process for the Tuas Water Reclamation to demonstrate the concept of low energy consumption and no chemical-recovery cleaning.
energy self-sufficient ?

## Slide 12: Case study 2: Tuas Water Reclamation Plant
  Treatment process: step-feed AO-MBR
TN & TP removal
No internal circulation
No external carbon addition
Promotes denitrifying polyphosphate accumulating organisms
HRT = 0.5 h
MLSS = 1,500 mg/L
Biological Wastewater Treatment
Online Course Series
Notes: The influent was raw used water. When the raw used water flows in the plant, it successively flows through a biologically-enhanced primary treatment before entering the MBR sector. The primary treatment includes biosorption (HRT 0.5h, MLSS 1500 mg/L), compact lamella plate primary clarifier, and a screen. Biologically-enhanced primary treatment maximizes the organic carbon capture and reduces the aeration requirement in the subsequent processes.
The MBR system is a step-feed AO-MBR system. A non-aerated zone and an aerated zone compose a pass, and there are five passes in the system. Then, the mixed liquor of the last pass flows into a submerged membrane tank. The step-feed AO-MBR
enhances the nutrient removal without the need for internal nitrate/nitrite circulation or external carbon addition. It also promotes denitrifying polyphosphateaccumulating organisms.
The MBR effluent is further treated by RO and reused for NEWater production. NEWater is the ultra-clean, high-grade reclaimed water to cushion the water supply in Singapore.

## Slide 13: Case study 2: Tuas Water Reclamation Plant
PVDF hollow fiber membrane
Pore size: 0.035 μm
Area: 26,396.2 m2
Flux: 20 L/m2·h (peak 30 L/m2·h)
Quality (mg/L)
TOC = 6.6
NH4+-N = 2.19
NO3—N = 1.19
NO2—N = 0.51
PO43—P = 0.17
MLSS = 2,000~5,000 mg/L
HRT = 5 h; SRT = 5~10 d
  Treatment process: step-feed AO-MBR
Biological Wastewater Treatment
Online Course Series
Notes: The operating parameters are shown in Table 13.5. The MLSS in the step-feed AO-MBR system is 2000~5000 mg/L, with total HRT of 5 h, and SRT of 5~10 d.
Regarding the membrane tank, PVDF hollow-fibre membranes with a nominal pore size of 0.035 μm are installed. The total effective surface area is 26,396.2 m2. The net flux is 20 l/m2.h and the peak flux can reach 30 l/m2.h.
The MBR effluent has a TOC concentration of 6.6 mg/L, ammonia 2.2, phospohorus less than 0.2 mg/L. Which is pretty clean.

## Slide 14: Case study 2: Tuas Water Reclamation Plant
HRT: 0.5 h
MLSS: 1,500 mg/L
Total energy consumption: 0.24~0.28 kWh/m3 (< 0.5 kWh/kg COD)
Air scouring energy: 0.04 kWh/m3
Maintenance cleaning:
200 mg/L NaOCl, twice/week
  Treatment process: step-feed AO-MBR
Biological Wastewater Treatment
Online Course Series
Notes: The energy consumption of the whole treatment process is in the range of 0.24-0.28 kWh/m3, or less than 0.5 kWh/kgCOD. Regarding the membrane tank, the air scouring energy consumption is as low as 0.04 kWh/m3. Maintenance cleaning using NaOCl is conducted twice per week, and no recovery cleaning was conducted between the start of operation in August 2017 and February 2020. The success of this Validation and Demonstration Plant supported the construction of Tuas Water Reclamation Plant. Let’s looking fordward to its commissioning.

## Slide 15
Course on Membrane Bioreactors
Practical application - 2
Jiao Zhang
Notes: We’ll have two more cases in this section.

## Slide 16: Contents
  Overall practical application
  Case study 1
  Case study 2
  Case study 3: A carrier-assisted MBR for industrial wastewater treatment
  Case study 4: A side-stream MBR for leachate treatment
  Case study 5
Biological Wastewater Treatment
Online Course Series
Notes: Different from last section, we’ll pay attention to industrial wastewater and leachate, which has higher concentrations of pollutants.

## Slide 17: Case study 3
  A MBR treatment plant belonging to Adama Agan Ltd.
    Location: Ashdod, Israel
    Commissioning time: 2012
    Capacity: 7,200 m3/d
A carrier-assisted MBR for industrial wastewater treatment
Biological Wastewater Treatment
Online Course Series
Notes: This wastewater treatment plant/facility is owned by Adama Agan Ltd., Ashdod, Israel. The company is an agriculture-related fine chemical producer. Because updated regulations required higher effluent quality, the former CAS processes were retrofitted as a dual aerobic sludge system, where MBR is applied. The project was carried out by Adama Agan and EPT (Environmental Protection Technologies), an Israeli based process engineering firm. The MBR retrofit plant was commissioned in 2012, with a treatment capacity of 7,200 m3/d.

## Slide 18: Case study 3: for industrial wastewater
  Treatment process: aerobic sludge system
MACarriers: membrane-accommodating carriers
to enhance the removal of recalcitrant COD
by biofilm’s adsorption and preconcentration
Also good for
Remove toxicity
Stabilize nitrification process
Biological Wastewater Treatment
Online Course Series
Notes: In this dual aerobic sludge system, the first sludge system consists of a micro-aerobic reactor, an aerobic reactor, and a gravity clarifier.
The effluent from the first sludge system flows into the second sludge system. The second sludge system is the MBR system. It consists of an aerobic tank, a post-anoxic tank, and a membrane tank. ZeeWeed membrane modules are installed.
In order to enhance the removal efficiencies of recalcitrant COD, membraneaccommodating carriers (MACarriers) are added to the reactor in the second sludge system. Dense and strong biofilm can be quickly formed on the huge bacteria-friendly surface area of MACarriers which can adsorb and preconcentrate the residual recalcitrant organic compounds in the mixed liquor. This process not only improves the effluent quality but also helps remove toxicity and make the nitrification process more stable.

## Slide 19: Case study 3: for industrial wastewater
AOX: absorbable organic halogens
Quality (mg/L)
COD = 3,500
NH4+-N = 10.5
TN = 236
TSS = 60
AOX = 50.4
Quality (mg/L)
COD: not available
NH4+-N = 0.5-2
TN < 20
TSS < 3
AOX = 3.5~5
  Treatment process: aerobic sludge system
Biological Wastewater Treatment
Online Course Series
Notes: The influent of the dual aerobic sludge system had a COD concentration as high as 3500 mg/L, which is approximately 10 times of that of municipal wastewater. The ammonia was 10 mg/L, TN about 240 mg/L, and AOX (absorbable organic halogens) was 50 mg/L.
After the treatment, ammonia was reduced to less than 2 mg/L, TN less than 20, and AOX 3.5~5 mg/L. Though COD data was not available, we can still tell the effective removal of pollutants of this treatment process.

## Slide 20: Case study 4
  A leachate treatment plant of Everbright Environmental Energy Co. Ltd.
    Location: Wuzhong Venous Industrial Park, Suzhou, China
    Commissioning time: 2014
    Capacity: 700 m3/d
A side‐stream MBR for leachate treatment
Biological Wastewater Treatment
Online Course Series
Notes: This case is a different one. The previous 3 caese are all submerged MBRs, which is also the extensively-used configuration. The next case is a side-stream MBR case.
The Waste-to-Energy project in the Wuzhong Venous Industrial Park, Jiangsu Province, is one of the largest solid waste incineration plants in China, with a designed treatment capacity of 3,550 t/d of solid waste when it was commissioned. The affiliated leachate treatment plant adopting MBR is owned and operated by Everbright Environmental Energy (Suzhou) Co.
Ltd. Commissioned in 2014, it has a designed treatment capacity of 700 m3/d.

## Slide 21: Case study 4: for leachate treatment
IOC: Internal and outer circulation anaerobic reactor.
  Treatment process: AO+UF
Number of reactors: 3 2 1
Effective volume
for each (m3)
1,900 800 2,400
Biological Wastewater Treatment
Online Course Series
Notes: Leachate flows successively into three parallel pretreatment tanks, three parallel internal and outer circulation (IOC) anaerobic reactors (effective volume: 1,900 m3 each), two parallel anoxic-aerobic tanks (effective volume: 800 m3 for each anoxic tank; 2,400 m3 for each aerobic tank), a UF unit, an NF unit and an RO unit. The treated water is totally reused, and zero liquid is discharged.
This MBR system is designed with a side-stream configuration, consisting of an A/O process and external UF units. The HRTs of A/O process is 1.92 d for the anoxic tank, and 5.89 d for the aerobic tank. The MLSS concentration is approximately 15,000 mg/l.
The UF units contain 18 tubular PVDF membrane modules with a total effective surface area of 490 m2. Cross-flow filtration is applied, and filtration and online cleaning are automatically controlled. The concentrated liquor is pumped back to the A/O tanks.

## Slide 22: Case study 4: for leachate treatment
  Treatment process: AO+UF
MLSS: 15,000 mg/L
18 tubular PVDF membrane modules
Area = 490 m2
Cross-flow filtration
HRT: 1.92 d, 5.89 d
Biological Wastewater Treatment
Online Course Series
Notes: Leachate flows successively into three parallel pretreatment tanks, three parallel internal and outer circulation anaerobic reactors (or we can call it IOC). Then it flows into two parallel anoxic-aerobic tanks, an Ultrafiltration unit, a Nanofiltration unit and a Reverse Osmosis unit.
The effective volumes of these reactors are 1,900 m3 for each IOC reactor, 800 m3 for each anoxic tank; and 2,400 m3 for each aerobic tank.
The treated water is reused.

## Slide 23: Case study 4: for leachate treatment
Quality (mg/L)
COD = 32,000
BOD = 15,000
NH4+-N = 1,500
TN = 1,800
SS = 22,000
Cl- = 6,500
Quality (mg/L)
COD = 13
BOD = 0
NH4+-N = 0.22
TN = 13
SS = 0
Cl- = 200
All reused, Zero liquid discharged
  Treatment process: AO+UF
Biological Wastewater Treatment
Online Course Series
Notes: Leachate has even higher concentrations of pollutants than industrial wastewater. The influent of this plant has a COD concentration of 32000 mg/L, BOD 15000 mg/L, ammonia 1500 mg/L, TN 1800 mg/L. We did not get the quality of the effluent of MBR system, but we can see that the effluent quality has been improved profoundly in this leachate treatment plant. COD has been reduced to 13 mg/L, ammonia 0.22, TN 13, which garantees the treated water to be totally resued, and the plant can achieve the goal of Zero Liquid Discharge.