## Slide 1
Course on Biofilms and Biofilm Reactors
Introduction to biofilms and biofilm reactors
Eberhard Morgenroth

## Slide 2
Photo: https://en.wikipedia.org/wiki/Grand_Prismatic_Spring

## Slide 3: Learning objectives
Explain differences and similarities between biological treatment processes using biofilms or suspended biomass
Discuss how mass transport limitations influence substrate availability
Get an overview of the overall course

## Slide 4: Learning from nature
Biofilm
Wastewater
Air
Lake with suspended biomass
Activated sludge treatment plant
Biofilm reactor
Biofilm in riverbed
Figures from Gujer

## Slide 5: Biological treatment processes
Necessary requirements for ALL biological treatment processes:
Avoid washing out biomass
Expose biomass to contaminants (electron donor)
Expose biomass to electron acceptor (e.g., oxygen or nitrate)
Biofilm reactors:
Higher biomass concentrations
Biofilms are usually mass transport limited
Activated sludge
Biofilm reactor

## Slide 6: Example: Biomass per reactor volume
Activated sludge
Conventional activated sludge: 3 – 5 g VSS/L
(Membrane bioreactor: 8 – 12 g VSS/L)
Example:
Biofilm thickness: LF = 1’500 μm
Specific surface area: aF = 300 m2/m3
Biofilm biomass density: XF = 30 g VSS/L
 Total biomass concentration: 13.5 g VSS/L
How much biomass per reactor volume?
Biofilm reactor

## Slide 7: Thick biofilms
Biofilm
Bulk liquid
Carrier
1’500 µm thick biofilm

## Slide 8: Thick biofilms where only the upper layers are penetrated by substrate
Bulk liquid
Carrier
1’500 µm thick biofilm
Biofilm
Substrate conc.
Distance from carrier

## Slide 9: Thick biofilms where only the upper layers are penetrated by substrate perform similar to thinner biofilms
Biofilm
Bulk liquid
Carrier
Active
Inactive
Bulk liquid
Carrier
Active
Inactive
1’500 µm thick biofilm
500 µm thick biofilm
Substrate conc.
Distance from carrier
Substrate conc.
Biofilm

## Slide 10: Active biomass per reactor volume
Example: Active biofilm thickness = 153 µm
Biofilm thickness: LF = 1’500 μm
Active biofilm thickness: LF,active = 153 μm
Total biomass concentration: 13.5 g VSS/L
 Active biomass concentration: 1.4 g VSS/L
1’500 µm
Note: Penetration depths of electron donor and acceptors depends on bulk phase concentrations and microbial processes
The value of 153 µm is from Table 17.5 and represents oxygen penetration depth into the biofilm for bulk phase oxygen concentrations of 5 mg O2/L

## Slide 11: Overall course outline
Overall mass balances: Linking microscale (biofilm scale) and macroscale (reactor scale) mass balances
Reactors: Biofilm reactor types and their relative design features
Modeling: Detailed mathematical modeling of diffusion and reaction in biofilms
Design: Practical design and mathematical modeling of biofilm reactors

## Slide 12: Take home messages
Biofilms grow on a carrier
Higher biomass concentrations in biofilm reactors
Biofilms are usually mass transport rather the biomass limited

## Slide 13
17: Modelling Biofilms
DOI:https://doi.org/10.2166/9781789060362_0757
18: Biofilm Reactors
DOI:https://doi.org/10.2166/9781789060362_0813

## Slide 14
Course on Biofilms and Biofilm Reactors
Micro- and macroscale mass balances for biofilm reactors
Eberhard Morgenroth

## Slide 15: Scales of observation
1 cm
This example is showing a moving bed biofilm reactor (MBBR)
10 m
Photos: AnnoxKaldnes
1 µm

## Slide 16: Learning objectives
Explain how micro and macro scale mass balances are linked for biofilm reactor
Calculate necessary biofilm surface area for target effluent concentrations and associated substrate flux into the biofilm

## Slide 17: Biofilm reactor: Linking micro- and macroscale
Control volume for macroscale mass balance
Control volume for microscale mass balance

## Slide 18: Macroscale mass balance
Example:
Influent flow rate: Q = 1500 m3/d
Influent COD concentration: SCOD,in = 200 mg COD/L
Desired effluent concentration: SCOD,out = 10 mg COD/L
Question:
How large should the reactor be to achieve the desired effluent concentration?
Control volume for macroscale mass balance
Biofilm surface area
Substrate flux into biofilm

## Slide 19: Microscale mass balance
Bulk liquid
Carrier
Biofilm
Biofilm surface
Flux of substrate into the biofilm (JLF)
Control volume for microscale mass balance
Control volume for microscale mass balance
Reactor bulk phase

## Slide 20: Microscale: Flux = f(bulk phase concentration)
Bulk liquid
Carrier
Biofilm
We can estimate COD flux into the biofilm (later in this course): JLF = 12 g COD/(m2.d)
Control volume for microscale mass balance
Control volume for microscale mass balance
Bulk phase COD concentration:
SB = 10 mg COD/L
The given value for JLF of 12 g COD/(m2.d) is in line with JLF,Hac in Table 17.5.

## Slide 21: Linking microscale and macroscale mass balances
Where:
JLF = Substrate flux into biofilm
AF = Total biofilm surface area
aF = Specific biofilm surface area = AF/V
V = Volume of the reactor
Sin = Influent substrate concentration
SB = Bulk phase substrate concentrations
 JLF = 12 g COD/(m2.d)

## Slide 22: Take home messages
Link micro and macroscale mass balance
Calculate biofilm surface
Calculate reactor volume
Later in this course
Type of reactor and reactor operation
Calculate substrate flux

## Slide 23
17: Modelling Biofilms
DOI:https://doi.org/10.2166/9781789060362_0757
18: Biofilm Reactors
DOI:https://doi.org/10.2166/9781789060362_0813

## Slide 24
Course on Biofilms and Biofilm Reactors
Biofilm reactors - Overview
Eberhard Morgenroth

## Slide 25
How to tell a biofilm to grow in a certain way?
Thin biofilm
Thick biofilm

## Slide 26: Learning objectives
Describe different categories of biofilm reactors
List four key requirements that are relevant for all biofilm reactors

## Slide 27: Biofilm reactor categories
(a1) Fixed media
(b) Fixed media during treatment interrupted by regular backwashing
(c) Moving carrier
E.g., Trickling filter
E.g., Biofilter
E.g., Moving bed biofilm reactor (MBBR)
(a2) Biofilm on gas permeable membrane
From Figure 18.2 in our textbook

## Slide 28: Four requirements that influence biofilm development and reactor performance
(Requirement #1) Large specific biofilm surface area
(Requirement # 2) Control biofilm thickness on carrier surface
  Suitable balance of biofilm growth and detachment
  Avoid clogging due to excessive biofilm accumulation
(Requirement # 3) Bring wastewater with contaminants into contact with biofilm surface
(Requirement # 4) Provide aeration (in case of aerobic processes)

## Slide 29: Biofilm reactor types
(a1) Fixed media
From Figure 18.2 in our textbook
Structured media
Rocks
Random pack plastic
Structured discs
Rotating biological contactor (RBC)
Trickling filter

## Slide 30: Biofilm reactor types
(a1) Fixed media
From Figure 18.2 in our textbook
(b) Fixed media during treatment interrupted by regular backwashing
Support media (4 mm diameter beads)
Rotating biological contactor (RBC)
Trickling filter
Biofilter

## Slide 31: Biofilm reactor types
(a1) Fixed media
(c) Moving carrier
From Figure 18.2 in our textbook
Moving bed biofilm reactor (MBBR)
Fluidized bed and airlift reactor
Biofilms without a carrier in SBR or continuous flow
(b) Fixed media with backwashing
Mobile carriers in continuous flow
Rotating biological contactor (RBC)
Trickling filter
Biofilter

## Slide 32: Biofilm reactor types
From Figure 18.2 in our textbook
Membrane attached biofilm reactor (MABR)
(a2) Gas permeable membrane
(a1) Fixed media
(c) Moving carrier
(b) Fixed media with backwashing
Rotating biological contactor (RBC)
Trickling filter
Biofilter

## Slide 33: Biofilm reactor types
From Figure 18.2 in our textbook
Membrane attached biofilm reactor (MABR)
(a2) Gas permeable membrane
(a1) Fixed media
(c) Moving carrier
(b) Fixed media with backwashing
Trickling filter
Rotating biological contactor (RBC)
Biofilter

## Slide 34: Take home messages
Biofilm reactor configuration, design, and operation determine biofilm features and ultimately biofilm reactor performance.
Need to consider four main requirements:
  specific surface area,
  biofilm thickness control,
  mixing, and
  aeration

## Slide 35
17: Modelling Biofilms
DOI:https://doi.org/10.2166/9781789060362_0757
18: Biofilm Reactors
DOI:https://doi.org/10.2166/9781789060362_0813

## Slide 36
Course on Biofilms and Biofilm Reactors
Biofilm reactors – Conventional reactor types
Eberhard Morgenroth

## Slide 37
https://openoregon.pressbooks.pub/nonmajorsenvirobiology/chapter/7-2-water-supply-problems-and-solutions/

## Slide 38: Learning objectives
Describe the main features of:
  Trickling filter
  Rotating biological contactor
  Biofilter
  Fluidized bed and air lift reactor
  Moving bed biofilm reactor (MBBR)
Explain how these biofilm reactors provide specific surface area, biofilm thickness control, mixing, and aeration

## Slide 39: Trickling filter using plastic or rock as media material
Plastic
Rock

## Slide 40: Factsheet: Trickling filter
Biofilm support | 
Biofilm thickness | 100 – 500 µm (can be up to 5’000 µm)
Biofilm thickness control | Spontaneous sloughing Limited concerns for clogging due to large void spaces
Mixing conditions | Rotating arms distribute influent over fixed biofilm support media Water flows (trickles) past the biofilm surface – plug flow
Aeration | Three phase system with natural convection of air
Treatment objectives |  carbon oxidation,  nitrification,  denitrification,  bio-P removal
Comments | Simple and robust operation, low maintenance, low energy consumption, high footprint

## Slide 42: Specific surface area for different types of reactors: aF = AF/V
Type of biofilm reactor | Size of material | Specific surface, aF (per reactor volume)
Trickling filter | 40 – 80 mm (rock) - (plastic) | 50 – 100 m2/m3 100 – 200 m2/m3
Rotating biological contactor (RBC) | - | 100 – 200 m2/m3
Biofilter | 1 – 8 mm | 1'000 – 3'000 m2/m3
Fluidized bed, airlift reactor | 0.2 – 0.8 mm | 3'000 – 4'000 m2/m3
Moving-bed biofilm reactor (MBBR) | 3.5 – 25 mm | 300 – 500 m2/m3
Aerobic granular sludge (AGS) | 0.2 – 5 mm (granule) | 100 – 3'000 m2/m3
Membrane-aerated biofilm reactor | - | 50 – 500 m2/m3

## Slide 43: Rotating biological contactors (RBC)
Up to 3.5 m diameter
Slow rotation
Biofilm on rotating disk
Optional: Aeration

## Slide 44: Factsheet: Rotating biological contractors (RBC)
Biofilm support | 
Biofilm thickness | 100 – 500 µm (can be up to 5’000 µm)
Biofilm thickness control | Spontaneous sloughing Limited concerns for clogging due to large void spaces
Mixing conditions | Disks rotate into and out of water (2 rpm)
Aeration | Exposure of biofilm to air while out of the water Some RBC provide additional aeration of the bulk phase
Treatment objectives |  carbon oxidation,  nitrification,  denitrification,  bio-P removal
Comments | Simple and robust operation, low maintenance, low energy consumption, smaller plants

## Slide 45: Biofilter: Biological treatment and filtration
Down-flow, dense media (Biocarbone®)
Up-flow, dense media (Biofor®)
Raw wastewater
Process air
Treated wastewater
Backwash water
Air scour
Backwash water extraction
During treatment
During backwashing
Water flow

## Slide 46: Biofilter: Configurations
Down-flow, dense media (Biocarbone®)
Up-flow, floating media (Biostyr®)
Up-flow, dense media (Biofor®)
Water flow
Nozzle system

## Slide 47: Biofilm carrier material in biofilters
A
B
C
Biofor® BioStyr®
(Submerged fixed bed, dense media) (Submerged fixed bed, floating media)
Diameter = 4 mm 4 mm 1 mm

## Slide 48: Factsheet: Biofilter
Biofilm support | Spherical support
Biofilm thickness | 50 µm (directly after backwashing) – 200 µm
Biofilm thickness control | Regular backwashing (every 24 – 48 h or depending on head loss)
Mixing conditions | Plug flow of water through packing, particle retention through filtration
Aeration | Bubble aeration
Treatment objectives |  carbon oxidation,  nitrification,  denitrification,  bio-P removal
Comments | No clarifier, low energy consumption, low footprint, limited to few technology providers, larger plants

## Slide 49: Specific surface area for different types of reactors: aF = AF/V
Type of biofilm reactor | Size of material | Specific surface, aF (per reactor volume)
Trickling filter | 40 – 80 mm (rock) - (plastic) | 50 – 100 m2/m3 100 – 200 m2/m3
Rotating biological contactor (RBC) | - | 100 – 200 m2/m3
Biofilter | 1 – 8 mm | 1'000 – 3'000 m2/m3
Fluidized bed, airlift reactor | 0.2 – 0.8 mm | 3'000 – 4'000 m2/m3
Moving-bed biofilm reactor (MBBR) | 3.5 – 25 mm | 300 – 500 m2/m3
Aerobic granular sludge (AGS) | 0.2 – 5 mm (granule) | 100 – 3'000 m2/m3
Membrane-aerated biofilm reactor | - | 50 – 500 m2/m3

## Slide 50: Fluidized bed and airlift reactors
Sand with biofilm

## Slide 51: Fluidized bed and airlift reactors
Circulation of water keeps biofilm carriers in suspension
Fluidized bed reactor
Airlift reactor

## Slide 52: Factsheet: Fluidized bed and airlift reactors
Biofilm support | Sand with biofilm
Biofilm thickness | 100 – 200 µm
Biofilm thickness control | Erosion and abrasion during turbulent mixing
Mixing conditions | Turbulent mixing, large upflow water velocities (10 – 50 m/h) by recirculating water or with an internal airlift
Aeration | Bubble aeration
Treatment objectives |  carbon oxidation,  nitrification,  denitrification,  bio-P removal
Comments | Low footprint, hydraulic control can be challenging in case of variable influent flow rates, used mostly for industrial wastewater treatment

## Slide 53: Specific surface area for different types of reactors: aF = AF/V
Type of biofilm reactor | Size of material | Specific surface, aF (per reactor volume)
Trickling filter | 40 – 80 mm (rock) - (plastic) | 50 – 100 m2/m3 100 – 200 m2/m3
Rotating biological contactor (RBC) | - | 100 – 200 m2/m3
Biofilter | 1 – 8 mm | 1'000 – 3'000 m2/m3
Fluidized bed, airlift reactor | 0.2 – 0.8 mm | 3'000 – 4'000 m2/m3
Moving-bed biofilm reactor (MBBR) | 3.5 – 25 mm | 300 – 500 m2/m3
Aerobic granular sludge (AGS) | 0.2 – 5 mm (granule) | 100 – 3'000 m2/m3
Membrane-aerated biofilm reactor | - | 50 – 500 m2/m3

## Slide 54: Moving bed biofilm reactor (MBBR) using suspended carrier media
Largest dimension from 0.5 to 2.5 cm
Carrier
Screen
Internal surface
Screen
Screen
Screen

## Slide 55: Types of biofilm carriers
Neutral buoyancy
Stable material
Internal surface area protecting biofilm
Prevent excessive biofilm accumulation
Large media specific surface area
Note: Reactor specific surface area (aF),
Mcquarrie, J. P. & Boltz, J. P. 2011. Moving Bed Biofilm Reactor Technology: Process Applications, Design, and Performance. Water Environment Research, 83, 560-575. and https://www.anoxkaldnes.com/en/technologies/z-mbbr

## Slide 56: Factsheet: Moving bed biofilm reactor (MBBR)
Biofilm support | 
Biofilm thickness | 100 – 500 µm
Biofilm thickness control | Erosion and abrasion during turbulent mixing
Mixing conditions | Completely mixed reactor with coarse bubble aeration or mechanical mixer, screens retain media in the reactor, typically separate tanks for carbon oxidation and nitrification
Aeration | Bubble aeration
Treatment objectives |  carbon oxidation,  nitrification,  denitrification,  bio-P removal
Comments | Robust operation, retrofitting of existing plants

## Slide 57: Specific surface area for different types of reactors: aF = AF/V
Type of biofilm reactor | Size of material | Specific surface, aF (per reactor volume)
Trickling filter | 40 – 80 mm (rock) - (plastic) | 50 – 100 m2/m3 100 – 200 m2/m3
Rotating biological contactor (RBC) | - | 100 – 200 m2/m3
Biofilter | 1 – 8 mm | 1'000 – 3'000 m2/m3
Fluidized bed, airlift reactor | 0.2 – 0.8 mm | 3'000 – 4'000 m2/m3
Moving bed biofilm reactor (MBBR) | 3.5 – 25 mm | 300 – 500 m2/m3
Aerobic granular sludge (AGS) | 0.2 – 5 mm (granule) | 100 – 3'000 m2/m3
Membrane-aerated biofilm reactor | - | 50 – 500 m2/m3

## Slide 58: Take home messages
Biofilms are retained in reactors with fixed or moving media
  Specific surface area (aF)
  Biofilm thickness control (detachment)
  Mixing conditions in the overall reactor and close to the biofilm surface
  Aeration
Factsheets with specific features and advantages of reactor technologies for trickling filters, rotating biological contactors, biofilters, fluidized bed and airlift reactors, and for moving bed biofilm reactors

## Slide 59: Factsheets

## Slide 60
17: Modelling Biofilms
DOI:https://doi.org/10.2166/9781789060362_0757
18: Biofilm Reactors
DOI:https://doi.org/10.2166/9781789060362_0813

## Slide 61
Course on Biofilms and Biofilm Reactors
Biofilm reactors – Hybrid systems combining biofilms with activated sludge
Eberhard Morgenroth

## Slide 62: Combine the best of both worlds?
Biofilm reactor
Activated sludge reactor

## Slide 63: Learning objectives
Explain approaches to retain both biofilms and activated sludge in a system using different types off biofilm systems
  Biofilm carriers that remain in a reactor (Moving bed biofilm reactor based)
  Biofilm carriers that move with the activated sludge (Mobile biofilms)
  Biofilms that develop without the addition of a biofilm carrier (Aerobic granular sludge)
Discuss similarities and differences of these approaches

## Slide 64: Moving bed biofilm reactor can also be with sludge recycle
IFAS operation:
Additional degree of freedom in operation by controlling sludge age of suspended biomass
Distinct ecological niches for bacteria
  Biofilm for slower growing bacteria
  Suspended growth for faster growing bacteria
Detached biomass from biofilm continuously seeds suspended biomass
Moving bed biofilm reactor (conventional operation)
Moving bed biofilm reactor with sludge recycle
= Integrated fixed film activated sludge (IFAS) system
= Hybrid system
Carrier
No carrier
No carrier

## Slide 65: From suspended carriers to mobile biofilm carriers
Mobile carriers would be lost through sludge wastage if there were no screens
Retention of biofilms and selective wasting of floccular biomass…
Integrated fixed film activated sludge (IFAS)

## Slide 66: Separators: How to retain mobile biofilm carriers?
Fine screen
Hydrocyclone
https://en.wikipedia.org/wiki/Hydrocyclone
Overflow (floc wastage)
Underflow (return sludge)
Feed
Feed
Return sludge
Floc wastage
Retention of biofilms and selective wasting of floccular biomass using fine screens or hydrocyclones

## Slide 67: Biofilms with or without carrier
Example of 1 mm organic particles as carrier material that can be retained by fine screens
Biofilms can grow on carrier material or develop as granules without a carrier inside
Biofilm
Carrier
No carrier inside

## Slide 68: Factsheet: Integrated fixed film activated-sludge
Biofilm support | 
Biofilm thickness | Depending on biofilm system
Biofilm thickness control | Erosion and abrasion during turbulent mixing, detachment from biofilm seeds activated sludge, attachment of flocs to the biofilm, separate control of activated sludge and biofilm biomass retention
Mixing conditions | Completely mixed reactor with coarse bubble aeration or mechanical mixer
Aeration | Bubble aeration
Treatment objectives |  carbon oxidation,  nitrification,  denitrification,  bio-P removal
Comments | Robust operation, retrofitting of existing plants, can have low energy consumption

## Slide 69: Aerobic granular sludge (AGS) in SBR
Granules without flocs
Photos: Layer, M. (2021) PhD dissertation, ETH Zurich. http://doi.org/10.3929/ethz-b-000474564, Livia Britschgi
Mixture of granules and flocs
(Granule removal)
Floc wastage
Effluent
AGS grown with volatile fatty acids
AGS grown with municipal wastewater
1 mm

## Slide 70: Factsheet: Aerobic granular sludge in SBR
Biofilm support | 
Biofilm thickness | 250 – 5’000 µm
Biofilm thickness control | Erosion and abrasion during turbulent mixing
Mixing conditions | Plug flow feeding, completely mixed reactor during react phase, different react phases, constant volume SBR
Aeration | Bubble aeration
Treatment objectives |  carbon oxidation,  nitrification,  denitrification,  bio-P removal
Comments | Low energy demand, retrofitting of existing plants, advantageous for concentrated wastewater

## Slide 71: How to determine the specific surface area in biofilm reactors where biofilms develop without a carrier?
Question: What is the specific surface area (aF)?
  Solids concentration, MLSS = 8 g/L
  Granule density, ρGranule = 90 g/L
  Granule diameter, dgranule = large (5 mm) or small (0.2 mm)
Answer:
aF = (6/dgranule) ∙ (MLSS/ρgranule)
= 100 m2/m3 (for very large granules, dgranule = 5 mm) = 3’000 m2/m3 (for small granules, dgranule = 0.2 mm)
Morgenroth, E. and Derlon, N. (2022) Entwicklung der biologischen Abwasserreinigung: Belebtschlamm vs Biofilmsysteme. Essener Tagung. https://www.dora.lib4ri.ch/eawag/islandora/object/eawag%3A24627, van den Berg et al. (2021) Density measurements of aerobic granular sludge. Environmental Technology, 1-11.
Sphere:
A = π∙d2
V = (π/6)∙d3
A/V = 6/d
If the biofilm surface is not directly related to the carrier surface (e.g., if there is no carrier) then biofilm surface can be estimated from aggregate concentration, density, and diameter

## Slide 72: Specific surface area for different types of reactors: aF = AF/V
Type of biofilm reactor | Size of material | Specific surface, aF (per reactor volume)
Trickling filter | 40 – 80 mm (rock) - (plastic) | 50 – 100 m2/m3 100 – 200 m2/m3
Rotating biological contactor (RBC) | - | 100 – 200 m2/m3
Biofilter | 1 – 8 mm | 1'000 – 3'000 m2/m3
Fluidized bed, airlift reactor | 0.2 – 0.8 mm | 3'000 – 4'000 m2/m3
Moving bed biofilm reactor (MBBR) | 3.5 – 25 mm | 300 – 500 m2/m3
Aerobic granular sludge (AGS) | 0.2 – 5 mm (granule) | 100 – 3'000 m2/m3
Membrane-aerated biofilm reactor | - | 50 – 500 m2/m3

## Slide 73: Combining biofilms with activated sludge
Reactor type | Moving bed biofilm reactor (MBBR) | Integrated fixed film activated sludge (IFAS) | Mobile biofilms in continuous flow | Aerobic granular sludge in continuous flow | Aerobic granular sludge in SBR
Biofilm | Yes | Yes | Yes | Yes | Yes
Carrier added | Yes | Yes | Yes | No | No
Activated sludge retention | No | Yes | Yes | Yes | Yes
Carrier/biofilm retention | Coarse screens in each compartment |  | Carrier/biofilm move with the activated sludge; fine screens or hydrocyclones to avoid removal with sludge wastage |  | Sedimentation
Operation | Continuous flow | Continuous flow | Continuous flow | Continuous flow | Sequencing batch

## Slide 74: Combining biofilms with activated sludge
Reactor type | Moving bed biofilm reactor (MBBR) | Integrated fixed film activated sludge (IFAS) | Mobile biofilms in continuous flow | Aerobic granular sludge in continuous flow | Aerobic granular sludge in SBR
Biofilm | Yes | Yes | Yes | Yes | Yes
Carrier added | Yes | Yes | Yes | No | No
Activated sludge retention | No | Yes | Yes | Yes | Yes
Carrier/biofilm retention | Coarse screens in each compartment |  | Carrier/biofilm move with the activated sludge; fine screens or hydrocyclones to avoid removal with sludge wastage |  | Sedimentation
Operation | Continuous flow | Continuous flow | Continuous flow | Continuous flow | Sequencing batch

## Slide 75: Combining biofilms with activated sludge
Reactor type | Moving bed biofilm reactor (MBBR) | Integrated fixed film activated sludge (IFAS) | Mobile biofilms in continuous flow | Aerobic granular sludge in continuous flow | Aerobic granular sludge in SBR
Biofilm | Yes | Yes | Yes | Yes | Yes
Carrier added | Yes | Yes | Yes | No | No
Activated sludge retention | No | Yes | Yes | Yes | Yes
Carrier/biofilm retention | Coarse screens in each compartment |  | Carrier/biofilm move with the activated sludge; fine screens or hydrocyclones to avoid removal with sludge wastage |  | Sedimentation
Operation | Continuous flow | Continuous flow | Continuous flow | Continuous flow | Sequencing batch

## Slide 76: Combining biofilms with activated sludge
Reactor type | Moving bed biofilm reactor (MBBR) | Integrated fixed film activated sludge (IFAS) | Mobile biofilms in continuous flow | Aerobic granular sludge in continuous flow | Aerobic granular sludge in SBR
Biofilm | Yes | Yes | Yes | Yes | Yes
Carrier added | Yes | Yes | Yes | No | No
Activated sludge retention | No | Yes | Yes | Yes | Yes
Carrier/biofilm retention | Coarse screens in each compartment |  | Carrier/biofilm move with the activated sludge; fine screens or hydrocyclones to avoid removal with sludge wastage |  | Sedimentation
Operation | Continuous flow | Continuous flow | Continuous flow | Continuous flow | Sequencing batch

## Slide 77: Take home messages
Integrated fixed film activated sludge (IFAS) systems combine the benefits of biofilms with the benefits of activated sludge
Additional degree of freedom in operation
  Growth conditions in biofilm
  Sludge age for growth conditions in activated sludge
There are different approaches to selectively retain biofilms.
Biofilms can grow with or without carrier

## Slide 78
11: Aerobic Granular Sludge
DOI:https://doi.org/10.2166/9781789060362_0497
17: Modelling Biofilms
DOI:https://doi.org/10.2166/9781789060362_0757
18: Biofilm Reactors
DOI:https://doi.org/10.2166/9781789060362_0813

## Slide 79
Course on Biofilms and Biofilm Reactors
Biofilm reactors – Membrane-attached biofilm reactors
Eberhard Morgenroth

## Slide 80
By Patrick J. Lynch, medical illustrator - Patrick J. Lynch, medical illustrator, CC BY 2.5, https://commons.wikimedia.org/w/index.php?curid=1496626

## Slide 81: Learning objectives
Explain how gas permeable membranes can be used to aerate biofilms
Discuss counter-diffusion of electron donors and acceptors in a biofilm
Explain how the gas phase can provide either electron acceptors or electron donors to the biofilm

## Slide 82: Membrane-attached biofilm reactor (MABR)
Bulk liquid
Biofilm
Flux of electron donor (e.g., COD or NH4+) into the biofilm (JLF)
Gas
Gas permeable membrane
Flux of electron acceptor (e.g., O2) into the biofilm
Can be applied for carbon oxidation and nitrification

## Slide 83: Membrane-attached biofilm reactor (MABR)
Bulk liquid
Biofilm
Flux of electron donor (e.g., COD or NH4+) into the biofilm (JLF)
Gas
Gas permeable membrane
Flux of electron acceptor (e.g., O2) into the biofilm
Can be applied for carbon oxidation and nitrification

## Slide 84: Membrane-attached biofilm reactor (MABR)
Bulk liquid
Biofilm
Flux of electron acceptor (e.g., NO3- into the biofilm (JLF)
Gas
Gas permeable membrane
Flux of electron donor (e.g., H2) into the biofilm
Can be applied for denitrification

## Slide 85: Membrane aerated biofilm reactor
https://www.suezwatertechnologies.com/products/biological/zeelung

## Slide 86: Factsheet: Membrane att. bio. react. (MABR)
Biofilm support | Hollow-fiber or spiral-wound gas permeable membranes
Biofilm thickness | 250 – 5’000 µm
Biofilm thickness control | Sloughing, erosion, and regular air scouring
Mixing conditions | Water flows past biofilm surface
Aeration | Through gas permeable membrane to the base of the biofilm, no dissolved oxygen in the bulk water
Treatment objectives |  carbon oxidation,  nitrification,  denitrification,  bio-P removal
Comments | Very low energy consumption, retrofitting of existing plants, suitable for concentrated wastewater, can be combined with activated sludge (i.e., possible IFAS configuration)

## Slide 87: Specific surface area for different types of reactors: aF = AF/V
Type of biofilm reactor | Size of material | Specific surface, aF (per reactor volume)
Trickling filter | 40 – 80 mm (rock) - (plastic) | 50 – 100 m2/m3 100 – 200 m2/m3
Rotating biological contactor (RBC) | - | 100 – 200 m2/m3
Biofilter | 1 – 8 mm | 1'000 – 3'000 m2/m3
Fluidized bed, airlift reactor | 0.2 – 0.8 mm | 3'000 – 4'000 m2/m3
Moving bed biofilm reactor (MBBR) | 3.5 – 25 mm | 300 – 500 m2/m3
Aerobic granular sludge (AGS) | 0.2 – 5 mm (granule) | 100 – 3'000 m2/m3
Membrane-attached biofilm reactor | - | 50 – 500 m2/m3

## Slide 88: Take home messages
Biofilm can grow on gas permeable membranes
MABR are operated with counter diffusion
Membranes can be used to transfer different compounds:
  O2 for carbon oxidation and nitrification
  H2 for denitrification
Energy efficient approach to supply oxygen compared to aeration

## Slide 89
17: Modelling Biofilms
DOI:https://doi.org/10.2166/9781789060362_0757
18: Biofilm Reactors
DOI:https://doi.org/10.2166/9781789060362_0813

## Slide 90
Course on Biofilms and Biofilm Reactors
Biofilm reactors –
Summary
Eberhard Morgenroth

## Slide 91: Learning objectives
Describe similarities and differences of the different biofilm reactor technologies
List treatment objectives that can be achieved with the different approaches

## Slide 92: Development of biofilm reactor technologies
Type of biofilm reactor | Spec. surface, aF | From… | Carrier | Detachment | Hybrid operation? | Treatment objectives
Trickling filter | 50 – 200 m2/m3 | 1900s | Fixed bed | Sloughing | Biofilm | C, N
Rotating biological contactor (RBC) | 100 – 200 m2/m3 | 1960s | Fixed bed | Sloughing | Biofilm | C, N
Biofilter | 1'000 – 3'000 m2/m3 | 1980s | Fixed bed with backwashing | Backwashing | Biofilm | C, N, DN
Fluidized bed, airlift reactor | 3'000 – 4'000 m2/m3 | 1980s | Fluidized media | Erosion and abrasion | Biofilm | C, N, DN
Moving bed biofilm reactor (MBBR) | 300 – 500 m2/m3 | 1990s | Suspended carrier | Erosion and abrasion | Biofilm | C, N, DN
MBBR based integrated fixed-film activated sludge (IFAS) | 300 – 500 m2/m3 | 1990s | Suspended carrier | Erosion and abrasion | Biofilm + activated sludge | C, N, DN, P
Aerobic granular sludge (AGS) in SBR or continuous flow | 100 – 3'000 m2/m3 | 2000s | ̶ | Erosion and abrasion | Biofilm + activated sludge | C, N, DN, P
Mobile carriers in SBR or continuous flow | 100 – 3'000 m2/m3 | 2010s | Mobile carrier moving with activated sludge | Erosion and abrasion | Biofilm + activated sludge | C, N, DN, P
Membrane-attached biofilm reactor (MABR) | 50 – 500 m2/m3 | 2010s | Biofilm on fixed gas-transfer membrane | Erosion, sloughing, and scouring | Biofilm + activated sludge | C, N, DN, P
Treatment objectives: C: Carbon oxidation, N: nitrification, DN: denitrification, P: EBPR

## Slide 93: Take home messages
Biofilm reactors have evolved over the past century
Selection of appropriate biofilm reactor technology should consider:
  Treatment objective and influent characteristics
  Complexity
  Flexibility
  Energy and cost
  Available space
  Climate conditions

## Slide 94: Do Exercise 17.4.13 in accompanying book of Examples and Exercises
Morgenroth, E. and Sorensen, K.H. (2023) Biological Wastewater Treatment: Principles, Modelling and Design - Examples & Exercises. Lopez-Vazque, C.M., Volcke, E., Wu, D., van Loosdrecht, M.C.M., Brdjanovic, D. and Chen, G.H. (eds).

## Slide 95
17: Biofilm modelling and biofilm reactors
DOI:https://doi.org/10.2166/9781789062304_0539
17: Modelling Biofilms
DOI:https://doi.org/10.2166/9781789060362_0757
18: Biofilm Reactors
DOI:https://doi.org/10.2166/9781789060362_0813

## Slide 96
Course on Biofilms and Biofilm Reactors
Diffusion and reaction in biofilms
Eberhard Morgenroth

## Slide 97: Oxygen concentration in the biofilm using microsensors
Larsen and Harremoes (1994) Water Research 28(6), 1435-1441.
5 µm

## Slide 98: Concentration profile in biofilm obtained from microelectrodes
Depth in μm
Dissolved oxygen concentration in g m-3
150
100
50
0
-50
-100
16
14
12
10
8
6
4
2
0
Biofilm
Wastewater
Larsen and Harremoes (1994) Water Research 28(6), 1435-1441.

## Slide 99: Learning objectives
Explain relevant processes determining concentration profiles inside the biofilm
  Diffusion (Fick’s first law)
  Biological degradation
Derive a mass balance equation considering diffusion and reaction in the biofilm
Assuming first order degradation kinetics:
  Calculate substrate concentrations inside the biofilm
  Calculate substrate flux into the biofilm

## Slide 100: Fick’s first law
Distance from surface (x)
Substrate concentration
0
SB
SF
Carrier
JF(x)
LF
x
bulk phase substrate concentration
concentration within biofilm
flux of substrate
Flux (JF): Rate of mass transport per cross sectional area
Fick’s first law: Flux goes from regions of high concentration to regions of low concentration, with a magnitude that is proportional to the concentration gradient (spatial derivative)
Biofilm
Bulk water

## Slide 101: Fick’s first law
Distance from surface (x)
LF x 0
SB
JF(x)
Substrate concentration
SF
Carrier
Biofilm
Bulk water

## Slide 102: Fick’s first law
Distance from surface (x)
LF x 0
SB
JF(x)
Substrate concentration
SF
Carrier
Biofilm
Bulk water

## Slide 103: Fick’s first law
Distance from surface (x)
LF x 0
SB
JF(x)
Substrate concentration
SF
Without concentration gradient, there is no diffusion and no flux
Carrier
Biofilm
Bulk water

## Slide 104: Fick’s first law
Distance from surface (x)
LF 0
SB
JF(x=LF)
No substrate diffuses into inert and impermeable biofilm support
Substrate concentration
SF
Carrier
Biofilm
Bulk water

## Slide 105: Biofilm mass balance for control volume
Control volume (∆x A)
Distance from surface (x)
SB
JF(x)
JF(x+∆x)
rF(x)
Substrate concentration
LF
Carrier
0
x
x+∆x
Biofilm
Bulk water

## Slide 106: Biofilm mass balance for control volume
Control volume (∆x A)
Distance from surface (x)
SB
JF(x)
JF(x+∆x)
rF(x)
Substrate concentration
LF x+∆x x 0
Carrier
Biofilm
Bulk water

## Slide 107: Biofilm mass balance for control volume
Control volume (∆x A)
Distance from surface (x)
SB
JF(x)
JF(x+∆x)
rF(x)
Substrate concentration
LF x+∆x x 0
Carrier
Biofilm
Bulk water

## Slide 108: Steady state material balance inside the biofilm

## Slide 109: Steady state material balance inside the biofilm

## Slide 110: Rate expressions
Zero-order
First-order
Substrate utilization assuming Monod growth kinetics
General rate expression for compound SF,i that is affected by multiple processes (j)

## Slide 111: Rate expressions
Zero-order
First-order
Substrate utilization assuming Monod growth kinetics
General rate expression for compound SF,i that is affected by multiple processes (j)

## Slide 112: Solution of diffusion reaction biofilm equation with first order reaction kinetics
Steady state: ∂SF/∂t = 0
Two boundary conditions
  BC #1: Substrate concentration at the biofilm surface is equal to bulk phase concentrations: SF(x=0) = SB
  BC #2: No substrate diffusion into the biofilm support: ∂SF/∂x(x=LF) = 0
Substrate degradation inside the biofilm has first order dependence on substrate concentration inside the biofilm: rF = (k1,FXF)∙SF (Note: k1,F and XF are both constants)
NOTE: In this lecture we neglect the effect of external mass transfer resistance and assume SLF = SB. Derivations in the book consider external mass transfer resistance with SLF < SB for boundary layer thickness LL > 0.

## Slide 113: Substrate concentrations inside the biofilm First order substrate removal
LF/Lcrit
SF/SB
x/LF

## Slide 114: Calculate flux into the biofilm applying Fick’s first law to the biofilm surface (x = 0)
Carrier
Distance from surface (x)
LF 0
SB
JF(x=0)
Substrate concentration
SF
Biofilm
Bulk water

## Slide 115: Substrate flux into biofilm First order substrate removal

## Slide 116: Substrate flux into biofilm
SB , mg/L
From Figure 17.8
 First order rate in biofilm results in first order dependence of substrate flux on SB

## Slide 117: Design example
You should design a biofilm reactor with the following characteristics
  Influent = 200 mg COD/L
  Target effluent = 3 mg COD/L (acetate)
  Influent flow rate = 1,500 m3/d
  Moving bed biofilm reactor (MBBR) with completely mixed bulk phase (aF = 300 m2/m3)
  LF = 400 µm thick biofilm
  First order rate constant, k1,F = 2.4 m3/g COD.d
  Biofilm biomass density, XF = 10,000 g COD/m3
  Diffusion coefficient for acetate in the biofilm, DF = 0.8 × 10-4 m2/d
Goal: Find volume of the biofilm reactor (VR)

## Slide 118: Microscale: Calculate substrate flux into biofilm

## Slide 119: Substrate flux in macroscale mass balance

## Slide 120: Summary of first order kinetics
Table 17.3: Summary of relevant solutions

## Slide 121: Summary of first and zero order kinetics
Table 17.3: Summary of relevant solutions

## Slide 122: Take home messages
Second order differential equation
Analytical solution for first order kinetics
  Substrate concentrations inside the biofilm SF(x)
  Substrate flux into the biofilm surface (JLF)
First order dependents of substrate flux into the biofilm

## Slide 123
17: Modelling Biofilms
DOI:https://doi.org/10.2166/9781789060362_0757
18: Biofilm Reactors
DOI:https://doi.org/10.2166/9781789060362_0813

## Slide 124
Course on Biofilms and Biofilm Reactors
Substrate concentrations and flux for zero order kinetics
Eberhard Morgenroth

## Slide 125: How are substrate flux and bulk phase concentrations related for different kinetics?
SB , mg/L
JLF, g/m2.d
?

## Slide 126: Learning objectives
Derive solutions for zero order biofilm kinetics
Calculate penetration depth (β·LF) into the biofilm

## Slide 127: Rate expressions
Zero-order
First-order
Substrate utilization assuming Monod growth kinetics
General rate expression for compound SF,i that is affected by multiple processes (j)

## Slide 128: Summary of first and zero order kinetics
Table 17.3: Summary of relevant solutions

## Slide 129: Penetration depth (β∙LF)
Biofilm
Bulk liquid
Carrier
Distance from surface (x)
LF βLF 0
SF(x)
SLF
SB
Active
Inactive

## Slide 130: Penetration depth (β∙LF)
Biofilm
Bulk liquid
Carrier
Distance from surface (x)
LF βLF 0
SF(x)
SLF
SB
Active
Inactive

## Slide 131: Zero order kinetics and boundary conditions for partially penetrated biofilm
Steady state: ∂SF/∂t = 0
Substrate concentration at the biofilm surface is equal to bulk phase concentrations: SF(x=0) = SB (Boundary condition #1)
Concentration gradient is zero at maximum substrate penetration: dSF/dx(x= βLF) = 0 (Boundary condition #2)
Substrate concentration is zero at maximum substrate penetration: SF(x= βLF) = 0 (Boundary condition #3)

## Slide 132: Solving 2nd order ordinary differential equation for partially penetrated biofilm
Note: The derivation here is for SB = SLF neglecting the influence of external mass transport resistance. The book (e.g., Eq. 17.9) does not make this simplifying assumption with SB > SLF.

## Slide 133: Solution for zero order (partial penetration): Flux
After substituting β this can be rearranged to
or

## Slide 134: Solution for zero order (full penetration): Concentration profile and flux
which can be rearranged to

## Slide 135: Solution for zero order (full penetration): Concentration profile and flux
which can be rearranged to

## Slide 136: Concentration profiles Zero order rates
SF/SB
x/LF

## Slide 137: Rate expressions
Zero-order
First-order
Substrate utilization assuming Monod growth kinetics
General rate expression for compound SF,i that is affected by multiple processes (j)

## Slide 138: Substrate flux into biofilm
200 µm biofilm. For details see Figure 17.8
SB , mg/L

## Slide 139: Substrate flux into biofilm
200 µm biofilm. For details see Figure 17.8
SB , mg/L

## Slide 140: Numerical solutions using AQUASIM

## Slide 141: Numerical solutions are readily available using commercial simulators
Biofilm reactor compartment
NH4+
CF(surface)
CF(base)
CB

## Slide 142: Take home messages
Zero order kinetics: differentiate partially or fully penetrated biofilm
Substrate flux
  Half order kinetics for partially penetrated biofilm (β < 1)
  Constant for fully penetrated biofilm (β ≥ 1)
Substrate penetration: Half order dependence on bulk phase concentration

## Slide 143
17: Modelling Biofilms
DOI:https://doi.org/10.2166/9781789060362_0757
18: Biofilm Reactors
DOI:https://doi.org/10.2166/9781789060362_0813

## Slide 144
Course on Biofilms and Biofilm Reactors
Substrate penetration and limiting substrate
Eberhard Morgenroth

## Slide 145: Bacteria require electron donor AND acceptor
NH4+
NO3-
O2

## Slide 146: Learning objectives
Calculate penetration depths for assuming zero order biofilm kinetics
Determine limiting substrate (electron donor or acceptor)
Calculate conditions where oxygen becomes limiting
Calculate flux of the non-limiting substrate
Discuss potential benefits of partial oxygen penetration

## Slide 147: Two component diffusion: What component is limiting?
NH4+
O2
O2
NH4+
Electron donor (NH4+) is limiting
Electron acceptor (O2) is limiting

## Slide 148: How deep will electron donors and acceptors penetrate into the biofilm?
Diffusion coefficient
Bulk phase concentration
Zero order rate constant
Biofilm biomass density

## Slide 149: Penetration depths for different types of growth
Penetration depth:
Table 17.5 in our textbook

## Slide 150: Is nitrification limited by the availability of electron donor or electron acceptor?
Penetration of NH4+ and O2
Oxygen limited for βNH4 > βO2

## Slide 151: Stoichiometry of nitrification from activated sludge model (ASM) matrix
Table 17.12 in our textbook

## Slide 152: Stoichiometry of nitrification from activated sludge model (ASM) matrix
Table 17.12 in our textbook

## Slide 153: Stoichiometry of oxygen and ammonia utilization

## Slide 154: Stoichiometry of oxygen and ammonia utilization

## Slide 155: Example: At what substrate concentration will oxygen (electron acceptor) become limiting?
Assume bulk phase oxygen concentration of 8 mg/L
Neglect external mass transfer resistance (RL = 0)
Calculate bulk phase concentrations above which a biofilm become potentially oxygen limited for the following electron donors
  Acetate
  Ammonium

## Slide 156: Example: At what concentration will oxygen (electron acceptor) become limiting?
 | Organic substrate removal | Nitrification
Electron donor | Organic substrate | NH4+
DF,e.d. | 0.8 · 94.1 · 10-6 m2/d | 0.8 · 169.1 · 10-6 m2/d
Electron acceptor | O2 | O2
DF,e.a. | 0.8 · 209.1 · 10-6 m2/d | 0.8 · 209.1 · 10-6 m2/d
α | 1 g O2/g COD | 4.57 g O2/g N
Y | 0.4 g COD/g COD | 0.22 g COD/g N
Electron acceptor limiting (based on Eq. 17.88) |  | 
Oxygen will be limiting (based on Eq. 17.88) assuming SLF,O2 = 8 mg/l for SLF,e.d. larger than | 29.6 mg COD/L | 2.3 mg N/L

## Slide 157: Example: At what concentration will oxygen (electron acceptor) become limiting?
 | Organic substrate removal | Nitrification
Electron donor | Organic substrate | NH4+
DF,e.d. | 0.8 · 94.1 · 10-6 m2/d | 0.8 · 169.1 · 10-6 m2/d
Electron acceptor | O2 | O2
DF,e.a. | 0.8 · 209.1 · 10-6 m2/d | 0.8 · 209.1 · 10-6 m2/d
α | 1 g O2/g COD | 4.57 g O2/g N
Y | 0.4 g COD/g COD | 0.22 g COD/g N
Electron acceptor limiting (based on Eq. 17.88) |  | 
Oxygen will be limiting (based on Eq. 17.88) assuming SLF,O2 = 8 mg/l for SLF,e.d. larger than | 29.6 mg COD/L | 2.3 mg N/L

## Slide 158: Example: How to calculate ammonia flux for oxygen limited nitrification?
Bulk phase O2 = 8 mg/L Bulk phase NH4+ = 5 mg N/L
Check limiting substrate looking at βNH4/βO2 or directly comparing βNH4 and βO2  Here βNH4/βO2 = 1.49  Oxygen limited
Calculate oxygen flux: JLF,O2 = 22.4 g O2/m2.d (e.g., from Table 17.5)
Calculate ammonia flux: Direct stoichiometric link between ammonia and oxygen utilization inside the biofilm (rF,NH4/rF,O2 = νNH4/νO2 = 1/(4.57 – YANO) and therefore JLF,NH4/JLF,O2 = rF,NH4/rF,O2  JLF,NH4 = JLF,O2/(4.57 – YANO) = 22.4/(4.57 – 0.22) = 5.2 g N/m2.d
Plausibility check: Achievable ammonia flux (5.2 g N/m2.d) is less than flux without oxygen limitation (7.6 g N/m2.d)

## Slide 159: Combined oxidation of organic carbon and ammonia
Bulk liquid
Carrier
Distance from surface (x)
LF 0
Heterotrophic B.
Inactive
Autotrophic B.
NH4+
O2
Organic carbon
Org carbon oxidation
Nitrification

## Slide 160: Partial penetration of oxygen can create favorable conditions for anammox
Bulk liquid
Carrier
Distance from surface (x)
LF 0
Anammox
AOB
NH4+
O2
NH4+
+
NO2-
=
N2
O2
N2

## Slide 161: Take home messages
Use β values to determine limiting substrate
Oxygen becomes limiting for
  COD > 29.6 mg COD/L
  NH4+ > 2.3 mg N/L
  …assuming bulk phase oxygen concentrations of 8 mg O2/L
Flux of non-limiting compound from stoichiometry

## Slide 162
17: Modelling Biofilms
DOI:https://doi.org/10.2166/9781789060362_0757
18: Biofilm Reactors
DOI:https://doi.org/10.2166/9781789060362_0813

## Slide 163
Course on Biofilms and Biofilm Reactors
Competition in biofilms
Eberhard Morgenroth

## Slide 164: Combined oxidation of organic carbon and ammonia
Bulk liquid
Carrier
Distance from surface (x)
LF 0
Heterotrophic B.
Inactive
Autotrophic B.
NH4+
O2
Organic carbon
Org carbon oxidation
Nitrification
What determines biofilm processes?
- Diffusion of soluble substrates
- Local growth of organisms

## Slide 165: Learning objectives
Discuss the relevance of partial substrate penetration for heterotrophic and autotrophic growth
Explain stratification of heterotrophic and autotrophic bacteria
Explain the relevance of bulk phase organic substrate concentrations on nitrification

## Slide 166: Numerical solutions are readily available using commercial simulators
Biofilm reactor compartment
NH4+
CF(surface)
CF(base)
CB

## Slide 167: Biomass distribution for low org. Carbon
Heterotrophic bacteria
Nitrifiers
Inert biomass
Bulk phase concentrations:
NH4+ = 13 mg N/L
Org C. = 3 mg COD/L
Oxygen = 8 mg O2/L
Carrier surface
Biofilm surface
Example 17.7 in our textbook based on Wanner and Gujer (1985) Wat.Sci.Tech. 17(2-3), 27-44.

## Slide 168: Biomass distribution for high org. Carbon
Heterotrophic bacteria
Nitrifiers
Inert biomass
Bulk phase concentrations:
NH4+ = 13 mg N/L
Org C. = 30 mg COD/L
Oxygen = 8 mg O2/L
Carrier surface
Biofilm surface
Example 17.7 in our textbook based on Wanner and Gujer (1985) Wat.Sci.Tech. 17(2-3), 27-44.

## Slide 169: Flux of ammonia strongly dependent on bulk phase organic carbon concentrations
JNH4 (g N/m2.d)
Only heterotrophic bacteria
Coexistence of heterotrophic and autotrophic bacteria
SB,COD (mg COD/L)
SB,NH4 (mg N/L)
Bulk phase oxygen = 8 mg O2/L

## Slide 170: Full scale observations
Based on Gonenc, E. and Harremoes, P. (1990) Nitrification in Rotating-Disk Systems .2. Criteria for Simultaneous Mineralization and Nitrification. Water Research 24(4), 499-505.
Full nitrification
No nitrification

## Slide 171: Take home messages
Competition of heterotrophic and autotrophic bacteria can be predicted using numerical modelling
Slower growing nitrifiers… …are outcompeted at high bulk phase organic substrate concentrations …grow deeper inside the biofilm where oxygen can become limiting
Competition must be considered in biofilm reactor design

## Slide 172
17: Modelling Biofilms
DOI:https://doi.org/10.2166/9781789060362_0757
18: Biofilm Reactors
DOI:https://doi.org/10.2166/9781789060362_0813

## Slide 173
Course on Biofilms and Biofilm Reactors
Detachment from biofilms
Eberhard Morgenroth

## Slide 174: What is balancing growth?
Carrier
JF(x=0)
?
Biofilm
Bulk liquid

## Slide 175: Learning objectives
Explain mechanisms of detachment
Prepare mass balance considering growth, decay, and detachment
Calculate steady state biofilm thickness

## Slide 176: Surface detachment
Biofilm
Bulk liquid
Carrier
Distance from surface (x)
LF 0
Mass balance:
Change of mass in biofilm =
Growth – Decay – Detachment

## Slide 177: A range of detachment models

## Slide 178: Predict biofilm thickness from mass balance
With ,
assuming steady state, and dividing by AFXF
Solving for steady state biofilm thickness, LF:

## Slide 179: Diversity of detachment mechanisms
Erosion and abrasion in a MBBR
Backwashing in a biofilter
Sloughing in a trickling filter
Breakup of large granule

## Slide 180: But detachment can be more complicated: Surface detachment and sloughing
Biofilm
Bulk liquid
Carrier
Distance from surface (x)
LF 0
Erosion
Sloughing

## Slide 181: Surface attachment of biomass and particulate organic substrate
Biofilm
Bulk liquid
Carrier
Distance from surface (x)
LF 0
Mass balance:
Change of mass in biofilm =
Growth – Decay + Attachment – Detachment
Organic particles: - attachment
- transport in biofilm
- hydrolysis
- detachment
Biomass (bacteria):
- attachment
- transport in biofilm
- detachment

## Slide 182: Detachment influences both the biofilm and bulk phase biomass
Bulk liquid
Carrier
Distance from surface (x)
LF 0
Heterotrophic B.
Inactive
Autotrophic B.
NH4+
O2
Organic carbon
Detachment is constantly “seeding” the bulk phase biomass  Relevant for integrated fixed film activated sludge (IFAS) systems

## Slide 183: Take home messages
Steady state biofilm modeling always considers biofilm detachment
Diversity of detachment rate models
Diversity of detachment mechanisms
Competition in biofilms is influenced by detachment
Many commercial biofilm simulators assume a constant biofilm thickness

## Slide 184: Take home messages
Modeling steady state biofilm always must consider biofilm detachment to balance growth
Detachment can be modeled explicit allowing to predict biofilm thickness
Assuming a constant biofilm thickness implicitly determines detachment, many commercial simulators use this approach
Explicit detachment rate expressions are often linked to biofilm thickness (LF or LF2)
Detachment and attachment are three-dimensional processes that are challenging to represent in one-dimensional biofilm models

## Slide 185
17: Modelling Biofilms
DOI:https://doi.org/10.2166/9781789060362_0757
18: Biofilm Reactors
DOI:https://doi.org/10.2166/9781789060362_0813

## Slide 186
Course on Biofilms and Biofilm Reactors
Influence of external mass transfer resistance
Eberhard Morgenroth

## Slide 187: Boundary layers
https://en.wikipedia.org/wiki/Boundary_layer
Hydrodynamic boundary layer

## Slide 188: Learning objectives
Explain why substrate concentrations at the biofilm surface are smaller than in the bulk liquid
Model substrate diffusion in the external mass transfer boundary layer
Link external mass transfer with substrate flux into the biofilm
Determine the relevance of external mass transfer resistance

## Slide 189: What is the influence of an external mass transfer boundary layer?
Biofilm
Bulk liquid
Carrier
Distance from surface (x)
LF 0
SF(x)
SLF
SB
Concentration profile assuming the concept of an external boundary layer
Actual concentration profile
Mass-transfer boundary layer
SLF < SB can be explained with external mass-transfer boundary layer

## Slide 190: Diffusion only in boundary layer
Biofilm
Bulk liquid
Carrier
Distance from surface (x)
LF 0
SF(x)
SLF
SB
Mass-transfer boundary layer
LL
SB-SLF

## Slide 191: Flux in mass-transfer boundary layer equals flux at biofilm surface
Linking flux in boundary layer (JBL) with flux at biofilm surface (JLF)
Assumptions: Steady state and first order biofilm kinetics
Extreme cases for boundary layer dominating or being negligible

## Slide 192: Two extreme cases
Biofilm
SF(x)
SLF
SB
LL
Biofilm
SF(x)
SLF
SB
LL

## Slide 193: Example: Influence of external boundary layer on substrate flux
Boundary layer thickness, LL (in μm)
External mass transfer resistance can have significant influence on substrate flux
Typical values: LL = 30 – 100 µm
Mixing conditions (e.g., aeration intensity) and biofilm morphology can have significant influence on boundary layer thickness
Bulk phase organic substrate (mg COD/L)
Flux of organic substrate (g COD/m2.d)
Biofilm with only heterotrophic substrate removal and LF = 200 μm (for further details see Figure 17.13 in the book)

## Slide 194: Take home messages
External mass transfer resistances significantly influence overall substrate removal rates
These resistances must be considered when applying biofilm models for reactor design or operation
The typical thickness of the external boundary layer LL = 30 – 100 µm (most reactors) – but depends on operation

## Slide 195
17: Modelling Biofilms
DOI:https://doi.org/10.2166/9781789060362_0757
18: Biofilm Reactors
DOI:https://doi.org/10.2166/9781789060362_0813

## Slide 196
Course on Biofilms and Biofilm Reactors
Modeling biofilm reactors
Eberhard Morgenroth

## Slide 197: Numerical modeling tools readily available
https://doi.org/10.25678/00021W (AQUASIM files), https://doi.org/10.25678/00022X (SUMO files)
O2
Bulk 1st layer 2nd 3rd 4th 5th 6th layer
6 x MBBR in-series
Sludge recycle

## Slide 198: Learning objectives
Describe how to use a numerical simulator to predict biofilm reactor performance
Understand how reactor design and operation impact effluent ammonia concentrations

## Slide 199: From analytical to numerical solutions
 | Analytical solutions of biofilm model… | Numerical solutions of biofilm model…
Kinetics | First or zero order kinetics | All kinetics
Substrates | Single limiting substrate User must identify limiting substrate | Multiple substrates
Bacterial groups | Single group of organisms | Multiple organisms
Dynamics | Only steady state | Include dynamic influent and operation
Type of solution | Explicit analytical solution | Must evaluate numerical model for each condition – no explicit analytical solution

## Slide 200: Example 17.9: What are the effects of heterotrophic/autotrophic competition?
The SUMO file used for these simulations is available at https://doi.org/10.25678/00022X
Sequence of moving bed biofilm reactor (MBBR)
Integrated fixed film activated sludge (IFAS) using sequence of MBBR

## Slide 201: Questions #1: Can the system achieve effluent ammonia concentrations below 1 mg N/L?
The SUMO file used for these simulations is available at https://doi.org/10.25678/00022X
Reference case

## Slide 202: Question #2: How to improve MBBR operation?
The SUMO file used for these simulations is available at https://doi.org/10.25678/00022X
Increase bulk phase O2 from 4 to 6 mg O2/L
Reference case
Increase biofilm surface area (AF)
COD removal and nitrification can be improved by adjusting MBBR design (increase AF) or operation (O2)

## Slide 203: Question #3: Effect of sludge recycle (IFAS)?
The SUMO file used for these simulations is available at https://doi.org/10.25678/00022X
IFAS operation
Reference case
COD removal and nitrification can be improved by increasing bulk phase biomass concentrations through IFAS operation

## Slide 204: Take home messages
Use simulators to answer practical design and operating questions
Nitrification can be improved by:
  Increasing biofilm surface area
  Increase bulk phase oxygen concentrations
  Recycling sludge from secondary clarifier

## Slide 205
17: Biofilm modelling and biofilm reactors
DOI:https://doi.org/10.2166/9781789062304_0539
17: Modelling Biofilms
DOI:https://doi.org/10.2166/9781789060362_0757
18: Biofilm Reactors
DOI:https://doi.org/10.2166/9781789060362_0813

## Slide 206
Course on Biofilms and Biofilm Reactors
Practical design of biofilm reactors
Eberhard Morgenroth

## Slide 207: Practical design and implementation
Predictions and understanding
Design and implementation

## Slide 208: Learning objectives
Explain factors influencing design surface loading
List ranges for typical design values
Discuss different design approaches:
  Separate design for carbon oxidation and nitrification
  Considering interactions of carbon oxidation and nitrification
JNH4, g N/(m2.d)

## Slide 209: Design using loading recommendations
Type of biofilm reactor | BOD loading (BA,COD) | Ammonia loading (BA,N) | Reference
BOD oxidation |  |  | 
Trickling filter | 4 g BOD/m2.d |  | ATV (1997)
Rotating biological contactor (RBC) | 8 – 20 g BOD/m2.d |  | Tchobanoglous et al. (2013)
Moving-bed biofilm reactor (MBBR) | 5 – 15 g BOD/m2.d |  | WEF and ASCE (1998)
Combined BOD oxidation and nitrification |  |  | 
Trickling filter | 2 g BOD/m2.d | - | ATV (1997)
Rotating biological contactor (RBC) | 5 – 16 g BOD/m2.d | 0.75 – 1.5 g N/m2.d | Tchobanoglous et al. (2003)
Moving-bed biofilm reactor (MBBR) | 4 g BOD/m2.d | 0.8 g N/m2.d | Odegaard (2006)
Tertiary nitrification |  |  | 
Trickling filter |  | 0.5 – 2.5 g N/m2.d | Tchobanoglous et al. (2013)
Rotating biological contactor (RBC) |  | 1.5 g N/m2.d | Tchobanoglous et al. (2013)
Appropriate design surface loading rates depend on
- desired effluent concentrations
- influent wastewater characteristics
- wastewater temperature
- reactor operation (e.g., bulk phase oxygen concentrations)

## Slide 210: Design using loading recommendations
Type of biofilm reactor | BOD loading (BA,COD) | Ammonia loading (BA,N) | Reference
BOD oxidation |  |  | 
Trickling filter | 4 g BOD/m2.d |  | ATV (1997)
Rotating biological contactor (RBC) | 8 – 20 g BOD/m2.d |  | Tchobanoglous et al. (2013)
Moving-bed biofilm reactor (MBBR) | 5 – 15 g BOD/m2.d |  | WEF and ASCE (1998)
Combined BOD oxidation and nitrification |  |  | 
Trickling filter | 2 g BOD/m2.d | - | ATV (1997)
Rotating biological contactor (RBC) | 5 – 16 g BOD/m2.d | 0.75 – 1.5 g N/m2.d | Tchobanoglous et al. (2003)
Moving-bed biofilm reactor (MBBR) | 4 g BOD/m2.d | 0.8 g N/m2.d | Odegaard (2006)
Tertiary nitrification |  |  | 
Trickling filter |  | 0.5 – 2.5 g N/m2.d | Tchobanoglous et al. (2013)
Rotating biological contactor (RBC) |  | 1.5 g N/m2.d | Tchobanoglous et al. (2013)

## Slide 211: Design using loading recommendations
Type of biofilm reactor | BOD loading (BA,COD) | Ammonia loading (BA,N) | Reference
BOD oxidation |  |  | 
Trickling filter | 4 g BOD/m2.d |  | ATV (1997)
Rotating biological contactor (RBC) | 8 – 20 g BOD/m2.d |  | Tchobanoglous et al. (2013)
Moving-bed biofilm reactor (MBBR) | 5 – 15 g BOD/m2.d |  | WEF and ASCE (1998)
Combined BOD oxidation and nitrification |  |  | 
Trickling filter | 2 g BOD/m2.d | - | ATV (1997)
Rotating biological contactor (RBC) | 5 – 16 g BOD/m2.d | 0.75 – 1.5 g N/m2.d | Tchobanoglous et al. (2003)
Moving-bed biofilm reactor (MBBR) | 4 g BOD/m2.d | 0.8 g N/m2.d | Odegaard (2006)
Tertiary nitrification |  |  | 
Trickling filter |  | 0.5 – 2.5 g N/m2.d | Tchobanoglous et al. (2013)
Rotating biological contactor (RBC) |  | 1.5 g N/m2.d | Tchobanoglous et al. (2013)

## Slide 212: Design assuming complete separation of carbon oxidation and nitrification
AF,COD = Q∙CODinfluent/BA,COD
AF,N = Q∙TKNinfluent/BA,N
AF,tot = AF,COD + AF,N
Vtot = AF,tot/aF
DWA (2001) Bemessung von Tropfkörpern und Rotationstauchkörpern, DWA, Hennef.
Heterotrophic
bacteria
Nitrifiers
Reality (gradient over reactor height)
Design assumption
VCOD
VN
← gradient →

## Slide 213: Design considering interactions of carbon oxidation and nitrification
Rusten et al. 2006. Design and operations of the Kaldnes moving bed biofilm reactors. Aquacultural Engineering, 34, 322-331.
For low organic load (0.4 g BOD5/(m2.d))
For high NH4+ concentrations (NH4+ is not limiting)
0 0.5 1 1.5 2 2.5 3
1.4
1.2
1
0.8
0.6
0.4
0.2
0
2.7
2.4
2.1
1.8
1.5
1.2
0.9
0.6
0.3
0
Bulk phase NH4+, mg N/L
Oxygen, mg O2/L
JNH4, g N/(m2.d)
JNH4, g N/(m2.d)
O2 = 6 mg/L
O2 = 4 mg/L
O2 = 2 mg/L
Organic load, g BOD5/(m2.d)
0
1
2
3
4
5
6
  0 2 4 6 8 10

## Slide 214:  Review background from previous lectures
Substrate penetration and limiting substrate
Competition in biofilms

## Slide 215: Review Chapter 17.8.2 Step‐by‐step approach to evaluating biofilm reactors
Decision support for choosing suitable analytical solution or combination of analytical solutions (Table 17.26)
For more complex situations, use simulators for numerical modeling
Table 17.26

## Slide 216: Factors influencing design decisions
Treatment objectives
  Carbon oxidation
  Nitrification
  Combined carbon oxidation and nitrification
  Biological carbon, nitrogen, and phosphorus removal
Dynamics
Temperature
Reactor type dependent factors
  Flexibility to control aeration and bulk phase oxygen concentrations
  External mass transfer resistance (LL)

## Slide 217: Take home messages
Tabulated surface loading rates provide initial estimates
Separate design for carbon oxidation and nitrification or stepwise approach
Design curves considering interactions of heterotrophic growth and growth of nitrifiers
Numerical modeling to evaluate different design choices

## Slide 218
Course on Biofilms and Biofilm Reactors
Parameters
Eberhard Morgenroth

## Slide 219: Are you ready to model?
Sumo example available at https://doi.org/10.25678/00022X

## Slide 220: Learning objectives
List relevant parameter values for different types of biofilm reactors

## Slide 221: Similar biological processes in biofilms and activated sludge systems
Can use most kinetic and stoichiometric parameters from activated sludge models
Half saturation constants in activated sludge models (i.e., KS in Monod equations) implicitly account for mass transport into flocs  Choose KS,biofilm < KS,activated sludge

## Slide 222: Identify parameters that have limited influence on model prediction
Example: Biofilm thickness does NOT have significant influence on model predictions for mass transport limited biofilms

## Slide 223: Typical biofilm thickness (LF)
Reactor type | Biofilm thickness, LF | 
 | Carbon oxidation | Nitrification
Trickling filter | 500 µm (top) 100 µm (low loaded bottom) | 100 – 200 µm (top) 20 – 40 µm (low loaded bottom)
Rotating biological contactor | 500 µm (first section) 100 µm (low loaded last section) | 100 – 200 µm (first section) 20 – 40 µm (low loaded last section)
Biological aerated filter (dense media) | 100 µm (before backwashing) 40 - 60 µm (after backwashing) | 20 – 40 µm
Biological aerated filter (floating media) | 100 – 200 µm | 80 – 120 µm
Moving bed biofilm reactors (MBBR) | 500 µm | 100 – 200 µm
Fluidized bed reactor, air lift reactor | 100 – 200 µm | 10 – 20 µm

## Slide 224: Typical boundary layer thickness (LL)
Typical values
  LL = 30 – 100 µm (most reactors)
  Lower values for higher mixing intensity and smoother biofilms
Dedicated experiments to evaluate the influence of mixing conditions on reactor performance  See section 17.11.3 for details
For well-defined hydrodynamic conditions, link RL with non-dimensional numbers characterizing mixing conditions (Reynolds number and Schmidt number)  See section 17.11.3 for details

## Slide 225: Specific surface area for different types of reactors: aF = AF/V
Type of biofilm reactor | Size of material | Specific surface, aF (per reactor volume)
Trickling filter | 40 – 80 mm (rock) - (plastic) | 50 – 100 m2/m3 100 – 200 m2/m3
Rotating biological contactor (RBC) | - | 100 – 200 m2/m3
Biofilter | 1 – 8 mm | 1'000 – 3'000 m2/m3
Fluidized bed, airlift reactor | 0.2 – 0.8 mm | 3'000 – 4'000 m2/m3
Moving-bed biofilm reactor (MBBR) | 3.5 – 25 mm | 300 – 500 m2/m3
Aerobic granular sludge (AGS) | 0.2 – 5 mm (granule) | 100 – 3'000 m2/m3
Membrane-attached biofilm reactor | - | 50 – 500 m2/m3

## Slide 226: Biofilm biomass concentration (XF)
XF = 20 – 30 g VSS/L for carbon oxidation
XF = 40 – 60 g VSS/L for nitrification, tertiary denitrification with methanol or with H2
Vbiofilm
Vreactor
Example: Volume fraction for MBBR with aF = 300 m2/m3 and LF = 500 µm:

## Slide 227: Take home messages
Use parameters from activated sludge models – except KS values
Biofilm thicknesses (LF) range from 20 – 500 m
External mass transfer boundary layer thicknesses (LL) range from 10 – 300 m
Biofilm biomass concentrations (XF) range
  from 20 – 30 g VSS/L for carbon oxidation and
  from 40 – 60 g VSS/L for nitrification, tertiary denitrification with methanol or H2

## Slide 228
Course on Biofilms and Biofilm Reactors
Acknowledgments
Kim Sørensen and Joshua Boltz for great discussions, critical feeback, and helpful input
MSc and PhD students at ETH Zürich and at the University of Illinois at Urbana-Champaign for suggestions and asking critical questions
Laura Baquedano for guidance on preparing video lectures and the actual video recording

## Slide 229
17: Modelling Biofilms
DOI:https://doi.org/10.2166/9781789060362_0757
18: Biofilm Reactors
DOI:https://doi.org/10.2166/9781789060362_0813

## Slide 230
Course on Biofilms and Biofilm Reactors
Acknowledgments
Kim Sørensen and Joshua Boltz for great discussions, critical feedback, and helpful input
MSc and PhD students at ETH Zürich and at the University of Illinois at Urbana-Champaign for suggestions and asking critical questions
Laura Baquedano for guidance on preparing video lectures, and the actual video recording and production