## Slide 1
Course on Wastewater Disinfection
Disinfection with UV Radiation, Sources of Germicidal (UV-C) Radiation
Ernest R. Blatchley III

## Slide 2
Gas Discharge Lamp Structure
Establishment of voltage between electrodes causes electron (e-) migration from cathode to anode
Electron interactions with gases lead to emission
Lamp components
  Lamp envelope
  Electrodes (cathode and anode)
  Noble gas
  Filling gas

## Slide 3
Lamp Components
Lamp envelope (often quartz or similar)
  Impermeable to gases
  Chemically compatible with filling gas
  Transparent
  Electrical insulator
  Able to withstand high T
Electrodes (cathode and anode)
  Usually made of Tungsten
    High melting point
    Low vapor pressure
Noble gas
  High ionization energy
  Chemically inert
Filling gas (Hg commonly used)
  Often added as liquid or solid (amalgam)
  Low ionization energy (metallic)
  High vapor pressure
  Inert toward other lamp components
  Energy gaps between excited states and lower energy states (e.g., ground state) correspond to useful wavelengths

## Slide 4
Energy Level Diagram for Mercury (Grotrian Diagram)
Collision between electron, filling gas (usually Ar) result in excitation, heating (e- + Ar  Ar*)
Collision between excited Ar or electrons with Hg atom causes excitation (Ar* + Hg  Hg*)
Relaxation of Hg* to lower-energy state causes photon emission
Photon energy (wavelength) depends on differences between energy states
Image from: Herzberg, G., Atomic Spectra and Atomic Structure.
Dover Publications: New York, 1944.

## Slide 5
Low Pressure Hg Lamp
Hg partial pressure: 10-3-10-2 Torr
Collision between electron, filling gas (usually Ar) result in excitation, heating
Collision between excited Ar or electrons with Hg atom causes excitation
Lamp output strongly affected by T (vapor pressure of Hg)
Ideal operating conditions
  Hg partial pressure  7 x 10-3 Torr
  40C
Output spectrum dominated by two transitions
  63P1  61S0 253.7 nm
  61P1  61S0 184.9 nm
  Other transitions allow minor emission in the visible
Most fluorescent lamps are LP Hg lamps with a fluorescent coating
Mercury amalgam lamps allow higher partial pressure of Hg
  LP HO lamps
  Same spectrum, higher power than conventional LP Hg lamps

## Slide 6
Medium Pressure Hg Lamp
Hg partial pressure  75 Torr
At start-up, output is similar to Low Pressure Hg lamp
Self-absorption causes rapid heating
Plasma temperature within lamp 5000-7000 K
Output spectrum contributions
  Relaxation of excited Hg to lower energy states (lines)
  Incandescence (continuum)
Thermal energy also contributes to electronic excitation of Hg
Spectrum is a combination of lines and a continuum
Broad hump at 200-245 nm due to ion-electron recombination
Broad hump at 250-270, with strong dip at 253.7 nm due to self-absorption (61S0  63P1 transition)

## Slide 7
Output Spectra of Hg Lamps (Normalized)
LP Hg lamp; Hg amalgam lamp
  Primary emission at 253.7 nm, 184.9 nm
  Secondary emissions in the visible
  Efficiency  30-35%
MP Hg lamp
  Broad spectrum, with distinct lines superimposed
  High temperature
  Efficiency 10%
LP Hg Lamp image from: https://uvsolutionsmag.com/articles/2019/
uv-low-pressure-lamps-offering-many-advantages-across-multiple-areas/
MP Hg Lamp image from: https://www.uvtechnik.com/en/products/uv-medium-pressure-lamps

## Slide 8
Concerns About Mercury
Minamata Convention = international treaty designed to control release of mercury, protect human health and environment
Called for elimination of Hg use in many applications
  Mining
  Coal-fired power plants
  Incineration
Hg-based lighting has not been banned, but granted an exemption
Pressure is increasing to eliminate Hg-based lamps
Need exists to develop alternative sources of UV, visible light

## Slide 9
Basic Characteristics of Excimer Lamps
Excimer = weakly-bound, electronically-excited dimer that is non-bonding or weakly-bonding in the ground state
Constituent gases are electronically excited to form excimer
Transition of excimer back to constituent gases in the ground state results on photon emission
Photon energy (wavelength) corresponds to energy gap between excimer and ground state gases (atoms)
Most excimer lamps involve rare gases (Rg), halogens (X), or rare gas/halogen mixtures (Rg/X)
Xe2* Lamp: Peak Output = 172 nm
Image from: https://www.ushio.com/
product/uv-172nm-excimer/

## Slide 10
Common Excimer Lamp Configurations
Dielectric Barrier-Discharge (DBD)
Often Annular Geometry
Inner electrode
Quartz sleeve (inner dielectric barrier)
Excimer gases
Quartz sleeve (outer dielectric barrier
Wire mesh electrode
High voltage between electrodes causes excitation
Flat Screen
Microcavities milled into quartz plate
Cavities filled with excimer gases
Electrodes around microcavities used to excite gases
Images from Park et al. (2017)
APL Photonics, 2, 041302,
https://doi.org/10.1063/1.4976530
Lamp Modules
Cavities within module filled with excimer gases
Peripheral electrodes excite excimer gases
Image from: https://www.ushio.com/
product/care222-filtered-
far-uv-c-excimer-lamp-module/

## Slide 11
Physics, Chemistry of Excimer Lamps
Rare gas (Rg) excimers
  Electronic excitation of Rg atom
  Transfer of kinetic energy from electron to Rg atom
  Three-body reaction to form excimer
  formation strongly dependent on Rg pressure
  Other excited intermediates formed, may contribute to excimer lamp emission
Rare gas/Halogen (Rg/X) mixtures
  Electronic excitation of Rg atom
  “Harpoon” reaction to form excimer
Output photon energy corresponds to the energy difference between
excimer and its constituent atoms in the ground state

## Slide 12
Characteristics of Excimer Lamps
No mercury
Output spectrum “selectable” based on constituent gases
Rapid on/off (< 1 s, typ.)
Wide range of shapes, sizes, form factors
Can be configured into a wide range of system geometries
Electrical efficiency highly variable, depends on excimer gas composition (10’s of %)
Image from: Vanesa Rueda (2016) MS Thesis,
Pontificia Universidad Javeriana
Image from Far UVC Technologies

## Slide 13
Electroluminescence
Electroluminescence is an optical process in which photons are generated as a result of passing an electrical current through a solid material
Common example = electronically-promoted formation of hole and (photo)electron, with subsequent recombination
Basic operating principle of light-emitting diodes (LEDs)
LEDs were originally developed for IR, then visible, now UV
Other luminescent phenomena: bioluminescence, chemiluminescence
Image from: https://aquisense.com/
uvc-led-technology/#benefits
Image from: https://blueocean.net/
bioluminescence-natures-fireworks-
from-fireflies-to-jellyfish/
Image from: https://www.
teachersource.com/product/
mini-light-sticks

## Slide 14
LEDs - Structure
All LEDs are diodes; allow electrical current to flow in one direction
Diodes are produced by ‘doping’ of semiconductor material (usually Si or Ge) with materials to allow formation of free electrons and electron holes
n-type semiconductor (negative): pentavalent impurity
p-type semiconductor (positive): trivalent impurity
Contact between p-type and n-type semiconductors yields a p-n junction

## Slide 15
LEDs – Photon Generation
Free electrons from n-type material diffuse toward p-type material
“Holes” from p-type material diffuse toward n-type material
Result is formation of a “depletion zone” in the vicinity of the p-n junction
“Barrier potential” from depletion zone prevents flow of electrical current
Barrier potential is a material property
  Si  0.7 V
  Ge  0.3 V

## Slide 16
LEDs – Photon Generation
Forward-Biased Condition: DC circuit with positive terminal connected to p-type material, negative terminal connected to n-type material
When applied voltage exceeds barrier potential, electrical current will flow
Current flow causes electrons and holes to migrate to p-n junction, resulting in recombination
Recombination of electrons and holes results in release of energy, sometimes in the form of a photon
Photon energy corresponds to bandgap, which is governed by dopant composition
Electrical efficiency is typically less than 5%, but rapidly evolving (improving)

## Slide 17: Output Characteristics of UV LEDs
Relative output spectra of UV LEDs. Values in the legend indicate the nominal peak wavelength of each LED, as indicated by the manufacturer. Horizontal reference line indicates 50% of maximum relative output. Parenthetical entries in legend indicate spectrum bandwidth at ½ maximum output. Data provided by AquiSense.
Bandgap energy (Eg, left) and corresponding wavelength (right) as a function of mole fraction of aluminum (x) in AlxGa1-xN films.
Images from: Blatchley (2023) “Photochemical Reactors: Theory, Methods, and Applications of Ultraviolet Radiation, Wiley, Hoboken, NJ, ISBN:9781119871309.
Equation from: Angerer et al. (1997) Applied Physics Letters 1997, 71, (11), 1504-1506.

## Slide 18: Summary
Hg lamps are the most common sources of UV-C radiation
  Electronically-efficient
  Generate radiation at useful wavelengths
  Concerns about Hg
Alternatives to Hg lamps
  Excimer lamps
  UV LEDs
  Tunable or selectable output, based on composition
  Lower electronic efficiency, but improving