## Slide 1
Course on Wastewater Disinfection
Disinfection with UV Radiation, Mechanisms and Kinetics
Ernest R. Blatchley III

## Slide 2
UV Disinfection
Common applications
  Drinking water production
  Wastewater disinfection
  Wastewater reuse
  Disinfection of air and surfaces
Mechanism of inactivation: Photochemical damage to critical biomolecules
  Nucleic acids (DNA, RNA)
  Proteins
Image from: https://earthobservatory.nasa.gov/features/UVB
Spectra derived from:
Setlow and Doyle Biochimica Et Biophysica Acta 1957, 24 (1), 27-41.
Voet et el. Biopolymers 1963, 1 (3), 193-208.

## Slide 3
Single-Event Model
Basis: one unit of photochemical damage is assumed to inactivate a microorganism/virus
For simplicity, assume we have a monochromatic source (i.e., emits one wavelength of UV radiation)
Kinetics of inactivation simulated as a pure photochemical reaction
= fluence rate (irradiance)
Rearranging, then integrating:
= UV “dose” (D)
Single-event model is a direct analog of Chick-Watson
Dose is the master variable

## Slide 4
Single-Event Model for Simulation of UV Disinfection Kinetics
MNV = murine norovirus (noroviruses are responsible for majority of waterborne and foodborne disease among humans)
MS2 = coliphage, common surrogate for human viruses
Image from: Weng et al. (2018) “Infectivity reduction efficacy of UV irradiation and peracetic acid-UV combined treatment on MS2 bacteriophage and murine norovirus in secondary wastewater effluent,” Journal of Environmental Management, 221, 1-9.
Data from: Malayeri et al. (2016) “Fluence (UV Dose) Required to Achieve Incremental Log Inactivation of Bacteria, Protozoa, Viruses and Algae,” IUVA News.

## Slide 5
Common Deviations from Single-Event Model
Shoulder, attributed to:
  Repair processes
  Requirement for multiple units of damage to cause inactivation
Tailing, attributed to:
  Population heterogeneity
  Particle association
Models have been developed to address these common deviations
k = -slope
shoulder
tailing

## Slide 6
Series-Event Model
Basis: some microbes are not inactivated until they accumulate multiple units of damage
A threshold dose is assumed to be required to initiate inactivation
Each photochemical event is assumed to follow 1st-order kinetics
All microbes with less than n units of damage retain viability
A series of differential equations leads to:
= microorganism with i units of damage
= energy associated with a single photon

## Slide 7
Series-Event Model
Series-event model provides a mechanistic explanation for shoulder
As n increases, the size of the shoulder increases
For the special case of n=1, the series-event model reduces to the single-event model
Bacteriophage f2
Escherichia
coli
Candida
parapsilosis
Modified from: Severin et al. (1983) “Kinetic Modeling of UV Disinfection of Water,” Water Research, 17, (11), 1669-1678.
1

## Slide 8
Two-Population Model:
  Sub-population A: Sensitive to UV exposure (series-event)
  Sub-population B: Resistant to UV exposure (single-event)
  Initial concentrations: A0 and B0
  N0 = A0 + B0
kA and kB are inactivation constants
“Shoulder” behavior is simulated using the series-event model
Phenotypic Persistence and
External Shielding Model
Sensitive Sub-Population
Persistent Sub-Population

## Slide 9: PPES Model Application
B. subtilis spores
222 nm
 254 nm
 282 nm
E. coli
Replicate Experiments
Images from: Pennell, K.G.; Aronson, A.I.; Blatchley III, E.R. (2007) “Phenotypic Persistence and External Shielding Ultraviolet Radiation Inactivation Kinetic Model,” Journal of Applied Microbiology, 104, 1192-1202.

## Slide 10
Summary
Inactivation of microorganisms, viruses by exposure to UV radiation is caused by photochemical damage to nucleic acids, proteins
Single-event model assumes one unit of photochemical damage will cause inactivation of a microbe or virus
Many microbes, viruses follow single-event kinetics well
Common deviations from single-event (1st-order) behavior observed in experiments include shoulder, tailing
Series-event model is mechanistically consistent with shouldering
PPES model is an example of a two-population model
UV doses required to inactivate most microbes, viruses are quite small
UV disinfection is a broad-spectrum antimicrobial, antiviral process