## Slide 1
Course on Wastewater Disinfection
Process Modeling: IDDF, CFD-E Models, Probabilistic Models
Ernest R. Blatchley III
Lyles School of
Civil Engineering
Environmental and
Ecological Engineering

## Slide 2: Disinfection Process Modeling
Requirements for “conversion” in disinfection systems (3-4 log10 units, typ.) are higher than in most other treatment processes; requires efficient reactors, optimization
Must account for relevant physical, chemical, microbiological phenomena
  Fluid mechanics, mixing
  Disinfectant “decay”
  Disinfection kinetics
  Kinetics of other reactions (disinfection byproduct [DBP] formation)
Software, hardware have advanced to the point that they can (should) be used as the foundation of disinfection system design
Image from: https://sswm.info/factsheet/disinfection-and-tertiary-filtration

## Slide 3: Residence Time Distribution Function (RTD)
Foundational to chemical disinfection process behavior
Concept: Knowledge of RTD and reaction kinetics allows
  Description of mixing behavior
  Accurate estimate of reactor performance
Experimental methods (tracer tests)
Numerical methods (Computational Fluid Dynamics [CFD])
Overall process simulation (Segregated-Flow Model)
A
B

## Slide 4: Integrated Disinfection Design Framework (IDDF)
Developed for drinking water chlorination; similar process dynamics in wastewater applications, other disinfectants
Basic components:
  Fluid mechanics, mixing
    Residence time distribution (RTD)
    Tracer tests
    CFD
  Disinfectant decay
  Intrinsic kinetics of disinfection, DBP formation
Simulation of process dynamics
Image from: https://www.wolkersdorfer.info/en/university/lectures/tshwane-university-of-technology.html?id=127

## Slide 5: IDDF Framework
IDDF References:
Bellamy et al. (2000) “Determining disinfection needs, J.AWWA, 92, 5, 44-52.
Ducoste et al. (2001) “The integrated disinfection design framework approach to reactor hydraulics characterization,” AQUA, 50, 4, 245-261.
dt
τ

## Slide 6: Computational Fluid Dynamics (CFD)
Equations of continuity, motion
Turbulence closure model
Discretize system
Define boundary and initial conditions
Link flow field conditions to scalar quantities
  Disinfectant reactions
  Pathogen reactions
Process optimization
  Disinfection efficacy
  Disinfectant consumption
  DBP formation
Images from: Angeloudis et al. (2014) “Predicting the disinfection efficiency range in chlorine contact tanks through a CFD-based approach,” Water Research, 60, 118-129.

## Slide 7: Numerical Simulations of UV Disinfection
Intrinsic kinetics
Influent target concentration
UV dose distribution
  Fluid mechanics (flow field)
  Fluence rate field
    Reactor geometry, configuration
    Flow rate
    Lamp type, power
    Optical characteristics of fluid being treated
Analogous to numerical simulations of chemical reactors
Accurate simulation of fluid mechanics is often more important than with chemical reactor (transport-limited processes)
Reactor Performance
Viable Target Concentration in Treated Water, N
Disinfection Kinetics
Influent Target
Concentration, N0
UV Dose
Distribution
Flow
Field
Fluence Rate Field
Reactor Geometry/
Configuration
Flow
Rate
Lamp Power
UVT
Image from: Blatchley III, E.R. (2023) Photochemical Reactors: Theory, Methods, and Applications of Ultraviolet Radiation, Wiley, Hoboken, NJ, ISBN: 978-1-119-87135-4.

## Slide 8
UV Arc
Reaction @ Lamp ID
Reaction @ Lamp OD
Air/Quartz Reaction
Quartz/Water Reaction
Ray Tracing: LP Hg Lamp
Fresnel Reflections at Every Optical Interface
Image from: Ahmed, Y.M.; Jongewaard, M; Li, M.; Blatchley III, E.R. (2018) “Ray Tracing for Fluence Rate Simulations in Ultraviolet Photoreactors,” Environmental Science & Technology, 52, 8, 4738-4745.

## Slide 9: Ray Tracing for Simulation of Fluence Rate Fields
Image from: Ahmed, Y.M.; Jongewaard, M; Li, M.; Blatchley III, E.R. (2018) “Ray Tracing for Fluence Rate Simulations in Ultraviolet Photoreactors,” Environmental Science & Technology, 52, 8, 4738-4745.

## Slide 10: Simulation of Disinfection Efficacy
Images from: Ahmed, Y.M.H.I.H. (2017) Stochastic Evaluation of Disinfection Performance in Large-Scale, Open-Channel UV Photoreactors, Ph.D. Dissertation, Purdue University, West Lafayette, IN

## Slide 11: Stochastic Evaluation Based on CFD-E Modeling
For a given set of input (operating) conditions, CFD-E model predictions are deterministic
Input parameters vary in real-world application
Stochastic approach: allow input parameters to vary
  Flow rate
  Lamp power
  UVT254
Allow process evaluation, including variability
  Improve process reliability
  Optimize operation (reduce cost)
Chart: Condition Number
| case1 | case2 | case3 | case4 | case5 | case6 | case7 | case8 | case9 | case10 | case11 | case12 | case13 | case14
AB | 13.26 | 10.81 | 3.67 | 0.94 | 1.41 | 2.5 | 1.824 | 0.573 | 0.956 | 41.66 | 5.49 | 13.3 | 3.016 | 0.344
CFD-I(No Variability) | 7.1358 | 21.5917 | 9.1219 | 0.6989 | 1.1623 | 2.3982 | 2.9987 | 0.35886 | 0.84561 | 23.473 | 1.974 | 3.2109 | 0.40581 | 0.11219
Max. Daily Limit | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235
Monthly Geometric Mean | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
Image from: Ahmed, Y.M.; Ortiz, A.P.; Blatchley III, E.R. (2019) “Stochastic Evaluation of Disinfection Performance in Large-Scale, Open-Channel, UV Photoreactors,” Journal of Environmental Engineering, ASCE, 145, 10, Article number 04019071.

## Slide 12: Summary
Disinfection process design is based on decomposition of process behavior (process engineering approach)
  Fluid mechanics
  Disinfection kinetics
  Kinetics of other reactions (DBP formation)
  Other relevant phenomena (e.g., fluence rate field for UV systems)
Experimental and computational tools allow accurate quantification of process behavior
Stochastic approaches are evolving to facilitate optimization of disinfection system design