## Slide 1
Course on Wastewater Disinfection
Dechlorination
Ernest R. Blatchley III

## Slide 2
Motivations for Dechlorination
Residual chlorine (free and/or combined) expresses toxicity toward aquatic organisms
Water quality is related to the health of fish and other forms of aquatic life
TL50 = Median Tolerance Limit
  Concentration at which 50% mortality is observed (96-hr exposure)
  May be influenced by temperature
Bluegill
Channel Catfish
Temperature (C) | TL50 (mg/L)
20 | 0.33
21 | 0.25
30 | 0.18
Temperature (C) | TL50 (mg/L)
20 | 0.09
30 | 0.09
TL50 data from: Roseboom and Richey (1977) Acute Toxicity of Residual
Chlorine and Ammonia to Some Native Illinois Fishes, Illinois Department
Of Registration and Education, Report of Investigation 85, ISWS/RI-85/77.

## Slide 3
Where is Dechlorination Applied?
Discharge of treated (chlorinated) water to surface water
  Rivers
  Streams
  Lakes
  Oceans
Common applications
  Wastewater effluents
  Cooling towers
Chlorine
Dechlorination

## Slide 4
Dechlorination Chemistry: Free Chlorine
Equilibrium lies far to the right
Forward reaction is extremely fast
Acid is produced (alkalinity is consumed)
Common form of dechlorinating agent:

## Slide 5
Dechlorination Chemistry: Combined Chlorine
Equilibrium lies far to the right
Forward reaction is fast, but not quite as fast as with free chlorine
Acid is produced (alkalinity is consumed, but not as much as with free chlorine)
Ammonia-N is a reaction product

## Slide 6
Summary
Residual chlorine (free or combined) is toxic to aquatic life
Dechlorination is often applied when treated water is discharged to surface water
Common applications include municipal wastewater effluents, cooling towers
Dechlorination stoichiometry based on reduced-S compounds is well-known
Dechlorination reactions with reduced-S compounds are fast
Process control of dechlorination is based on flow rate and residual chlorine concentration