## Slide 1
Course on Wastewater Disinfection
Disinfection with Peracids, Formation/Degradation
Ernest R. Blatchley III

## Slide 2
Motivations for Use of Alternative Disinfectants
Chlorine is (by far) the most commonly applied disinfectant in large-scale, municipal-scale applications
Disadvantages of chlorine
  Residual toxicity
  DBP formation
  Need to dechlorinate
  Recalcitrant microorganisms
From: Blatchley et al. (1997) “Effects of Disinfectants on
Wastewater Effluent Toxicity,” Water Research, 31, 7, 1581-1588.
Image from: https://aquaria.com.ua/corm.images/
%C4%E0%F4%ED%E8%E8/Ceriodaphnia%20dubia.jpg
Ceriodaphnia
dubia

## Slide 3
Microbial Resistance to Chlorine
Chlorine effective for control of (vegetative) bacteria and viruses
  Ct 1-2 mgmin/L  3-4 log10 units
Protozoan parasites tend to be quite resistant to chlorine
  Cryptosporidium parvum
  Giardia lamblia
Protozoan parasites are responsible for a large fraction of waterborne disease
Some bacterial spores are also chlorine-resistant
Data from: Murphy et al. (2015) “Effect of Cyanuric Acid on the
Inactivation of Cryptosporidium parvum under Hyperchlorination
Conditions,” Environmental Science & Technology, 7348-7355.

## Slide 4
Peracids as Alternative Disinfectants
Peracids include 1 or more peroxy groups
Behave as weak acids
Structural and functional similarity to hydrogen peroxide
Produced by reaction between carboxylic acid and H2O2
Equilibrium rapidly established
Free radicals also produced
Synergism among peroxy compounds, H2O2, and radicals
Broad-spectrum antimicrobial characteristics
Minimal DBP formation
  Carboxylic acids (natural degradation)
  Aldehydes (peracids + NOM)

## Slide 5
Peracetic Acid Disinfection: Applications
Image from: https://www.foodsafety
magazine.com/signature-series/
peracetic-acid-in-the-fresh-food-industry/
Food Processing, Preservation
Image from: https://www.steris.com/
healthcare/products/endoscope-
reprocessing/liquid-chemical-sterilization
Medical Instruments
Pulp and Paper Processing
Image from: https://www.indiamart.com/
proddetail/peracetic-acid-12-for-pulp-and-
paper-industry-17355797991.html
Cooling Towers
Image from: https://envirotech.com/
product/brommax-10-2/cooling-tower/
Image from: https://www.waterworld.com/drinking-water/treatment/article/16191281/benefits-of-peracetic-acid-for-municipal-wastewater-disinfection
Municipal Wastewater

## Slide 6
Peracid Formation
Produced by reaction between carboxylic acid and
General chemistry of formation:
Peracid () compounds display weak acid behavior
Equilibria are established rapidly between acid (neutral) and conjugate base (anionic) forms

## Slide 7
Peracetic Acid (PAA) Formation
Most commonly applied peracid is peracetic acid (PAA)
PAA is a weak acid

## Slide 8
Other Peracids
Performic Acid (PFA)
Perpropionic Acid (PPA)
Neutral forms of peracids tend to be most effective as disinfectants
Peracid stability tends to increase with aliphatic chain length; but longer chain length also leads to higher residual organic carbon
Peracetic Acid (PAA) is the most commonly used peracid because it generally provides the best balance among these characteristics

## Slide 9
Autodecay of Peracids
Cleavage of peroxy bond
Reactions with aqueous constituents yield other radicals, reactive oxygen species (ROS)
  Superoxide anion
  Hydroperoxyl radical
  Acyl and peracyl radicals

## Slide 10
Disinfection by Peracids
Appears to involve synergism among peracids, H2O2, and radicals
HO appears to play important roles in disinfection
Microbial inactivation is accomplished by
  Oxidation of sulphydryl (-SH) and sulfur (S-S) groups in enzymes
  Denaturation of proteins
  Disruption of osmosis (membranes)
  Nucleic acid damage
Radical intermediates are also responsible for oxidation by peracids

## Slide 11
Summary
Alternatives to conventional chlorination are sought to address the limitations of the process
  Toxicity associated with residual chlorine and DBPs
  Recalcitrant microbes (resting stages of bacteria, protozoa)
Peracids are used as substitutes for chlorine in disinfection of water not intended for human consumption
  Broad-spectrum antimicrobial characteristics
  Minimal DBP formation
Peracids are used in many other disinfection applications
Peracids are formed by reactions between carboxylic acids and hydrogen peroxide
  Reactions are readily reversible
  Reach equilibrium quickly
Peracids are weak acids; protonated (neutral) forms are generally most effective as disinfectants
Stability and residual organic carbon are influenced by aliphatic chain length; PAA generally represents the best compromise among these characteristics
Autodecay of peracids results in formation of reactive radical intermediates
Disinfection is attributable to the combined effects of the peracids themselves, H2O2, and the degradation products (radicals)
Radical intermediates are also important to the function of peracids as oxidants